## Schedule_1_SS
SCHEDULE NO. 1
PLANT, EQUIPMENT AND MANDATORY SPARE PARTS SUPPLIED FROM ABROAD
FOR NEW KILIFI SUBSTATION
Note 1: All proposed mandatory spare parts for each equipment or system shall be specified in detail by Bidders.
Note 2: All main and spare equipment shall be provided for proper operation in 1000m altitude. In case of other range may has been mentioned in the schedules of technical information (Part 2-E), the higher altitude category shall be considered.
Note 3: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Item No | Description | Country of Origin | Unit | Estimated Quantity | Foreign Currency (FC1) = USD (FC2) = EURO |  | Total Price
[5 empty] | Foreign Manufacture |  | Foreign Manufacture
[5 empty] | Unit Price (CIP) |  | (Quantity x Unit Price)
[5 empty] | FC1 | FC2 | FC1 | FC2
EQUIPMENT AND MATERIAL
1 | 220kV PRIMARY PLANT
1.1 | 220kV Circuit Breaker (3 phase) 2500A, 40kA - single pole |  | No. | 6
1.2 | Motorized disconnector (3-phase) 220kV,2500A,40kA, with two (2) earthing switch with earth mat |  | Set | 4
1.3 | Motorized disconnector (3-phase) 220kV,2500A,40kA, with one (1) earthing switch, and earth mat |  | Set | 12
1.4 | 220kV, 40kA Motorized earthing switch (3-phase) with earth mat |  | Set | 2
1.5 | Surge arrester 220kV (1-phase) including surge counter and earth leakage meter |  | No. | 12
1.6 | Post Insulator |  | Lot | 1
1.7 | Insulator string (suspension and strain types with hardware fitting) |  | Lot | 1
1.8 | 220 kV Post type current transformer, for protection and metering, five cores (1-phase) |  | No. | 18
1.9 | 220 kV Post type current transformer, for metering, two cores (1-phase) |  | No. | 6
1.10 | 220 kV Capacitive voltage transformer protection and metering three cores (1-phase) |  | No. | 6
1.11 | 132 kV Capacitive voltage transformer protection and measuring two cores (1-phase) |  | No. | 18
1.12 | Conductor - Tubular |  | Lot | 1
1.13 | Conductor - Stranded |  | Lot | 1
1.14 | Connectors and clamps for tubular conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
1.15 | Connectors and clamps for stranded conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
TOTAL PRICE ITEM 1
2 | 132kV PRIMARY PLANT
2.1 | 132kV Circuit Breaker (3 phase) 1250A, 31.5kA |  | Set. | 3
2.2 | Motorized disconnector (3-phase), without earth switch, with earth mat |  | Set | 6
2.3 | Motorized disconnector (3-phase), complete with one integral motorised earth switch, and earth mat |  | Set | 2
2.4 | 132kV, 31.5kA Motorized earthing switch (3-phase) with earth mat |  | Set | 2
2.5 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 6
2.6 | Post insulator |  | Lot | 1
2.7 | Insulator string (suspension and strain types with hardware fitting) |  | Lot | 1
2.8 | Post type current transformer protection and metering five cores (1-phase) |  | No. | 3
2.9 | Post type current transformer, for protection, four cores (1-phase) |  | No. | 6
2.10 | Post type current transformer, for protection,two cores (1-phase) |  | No. | 6
2.11 | Voltage transformer Protection and metering Two Cores (1-phase) |  | No. | 6
2.12 | Conductor - Stranded |  | Lot | 1
2.13 | Connectors and clamps for stranded conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
TOTAL PRICE ITEM 2
3 | AUTOTRANSFORMER (A.TR.)
3.1 | Autotransformer three phase units HV220/MV132/TV11kV, 90-110MVA including HV/MV/TV/Neutral Bushing CT's, OLTC, RTCC, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS |  | No. | 2
3.2 | Fire Detection and Protection System (Nitrogen Injection system) |  | Lot | 2
3.3 | 50 kg wheeled Dry-Powder Fire extinguisher for Power Transformer |  | No. | 2
TOTAL PRICE ITEM 3
4 | EARTHING & AUXILIARY TRANSFORMER
4.1 | 11/0.415kV, 500kVA, ZNyn11 Earthing & Auxiliary transformers including all accessories as required |  | No. | 2
4.2 | 11kV, 30A 3-phase cut off fuse |  | No. | 6
4.3 | 50 kg wheeled Dry-Powder Fire extinguisher for Auxiliary transformer |  | No. | 2
4.4 | 500A/10s Neutral Earthing Resistor (NER) including all accessories as required |  | No. | 2
TOTAL PRICE ITEM 4
5 | 220kV & 132 PROTECTION SYSTEMS
5.1 | 220kV Diameter (OHL) Protection System including:
5.1.1 | Main 1 21L Protection(with all required functions as per PSLD) |  | No. | 2
5.1.2 | Main 2 87L Protection(with all required functions as per PSLD) |  | No. | 2
5.1.3 | 87T/87NT protection with all required functions as per PSLD |  | No. | 2
5.1.4 | 87HVC protection with all required functions as per PSLD |  | No. | 2
5.1.5 | Auto-Reclose Protection Relay(with all required functions and Voltage Selection Logic as per PSLD) |  | No. | 2
5.1.6 | All other relays or functions such as over voltage; under voltage; trip relay; trip circuit supervison; pole discordance; synchro check; fuse failure; close relay; lockout relay; short zone, end zone; circuit breaker failure, cubicles, test blocks and test plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the full protection scheme. |  | Lot | 1
5.1.7 | Panels including all accessories ACC the PSLD, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 12
5.1.8 | Equipment for modification works in remote existing Malindi, substation including name tags, differential relays settings and etc.. |  | Lot | 1
5.2 | Transformer 132kV Side and Neutral Earthing Transformer Protection System including:
5.2.1 | Main 87LVC Protection(with all required functions as per PSLD) |  | No. | 2
5.2.2 | Backup 67/67(N) Protection(with all required functions as per PSLD) |  | No. | 2
5.2.3 | Earth Fault 50N/51N (SBEF) Protection (with all required functions as per PSLD) |  | No. | 2
5.2.4 | 50TV protection with all required functions as per PSLD |  | No. | 2
5.2.5 | 87NTV protection with all required functions as per PSLD |  | No. | 2
5.2.6 | All other relays or functions such as over voltage; under voltage; trip relay; trip circuit supervison; pole discordance; synchro check; fuse failure; close relay; lockout relay; short zone, end zone; circuit breaker failure, cubicles, test blocks and test plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the full protection scheme. |  | Lot | 1
5.2.7 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 5
5.3 | 220kV & 132kV Busbar Protection System
5.3.1 | 220kV Busbar Protection System
5.3.1.1 | 220kV Low Impedance type Busbar Protection Relay ACC. To PSLD drawing and considering future extension |  | No. | 2
5.3.1.2 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux relays, test and terminal blocks, timers, wiring etc. to make the system complete |  | No. | 2
5.3.2 | 132kV Busbar Protection System
5.3.2.1 | 132kV Low Impedance type Busbar Protection Relay ACC. To PSLD drawing and considering future extension |  | No. | 2
5.3.2.2 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux relays, test and terminal blocks, timers, wiring etc. to make the system complete |  | No. | 2
5.4 | Miscellaneous modification works as necessary to make a complete functional 220 &132kV protection system |  | Lot | 1
TOTAL PRICE ITEM 5
6 | AVR PROTECTION SYSTEMS
6.2 | Autotransformer Automatic Voltage Regulation System including:
6.2.1 | Automatic Voltage Regulator Relay (AVR) |  | No. | 2
6.2.2 | Panels with all accessories and auxiliaries, lighting, heating, socket, push buttons, wiring, terminals, test facilities, discrepancy and all other switches, labels, unit measurement indicating lamps, position indicators, alarm announciators, temperature indicators, test block/plug , Labels, etc. and with the following equipment. |  | No. | 2
TOTAL PRICE ITEM 6
7 | 220/132kV SUBSTATION CONTROL SYSTEM
7.1 | Substation automation system including:
7.1.1 | All software and license, Modifications in HMI |  | Lot | 1
7.1.2 | Bay Control and Protection Units (BCU/BCPU)(with all required functions as per PSLD) |  | No. | 6
7.1.3 | Bay Control Panels |  | No. | 2
7.1.4 | Auxiliary and Common Services Bay Control Unit |  | Lot | 1
7.1.5 | Auxiliary and Common Services Panel including all accessories |  | Lot | 1
7.1.6 | Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) |  | Lot | 1
7.1.7 | Human Machine Interface Systems and Computers |  | No. | 2
7.1.8 | Any other material for full functionality of the Substation Control System |  | Lot. | 1
7.1.9 | Fault Monitoring System and Alarm System |  | Lot | 1
8 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
8.1 | Equipment for Modification works at Remote SS |  | Lot | 1
9 | TELECOMMUNICATION & NCC/RCC/NSCC
9.1 | Required equipment for Telecommunication and Teleprotection Signalling System |  | Lot | 1
9.1.1 | Required equipment for Telecommunication SDH System |  | Lot | 1
9.1.2 | Required equipment for Teleprotection Signalling Equipment Interface Board for Distance & Differential protection relay |  | Lot | 1
9.2 | New Firewall system with all necessary Licenses |  | Lot | 1
9.3 | Required equipment for incorporating substation equipment into the SCADA/EMS System at the NCC/RCC/NSCC |  | Lot | 1
9.4 | Required equipment for modifications to NCC/RCC/NSCC mimic board (if any) |  | Lot | 1
9.5 | All necessary licences, hardware, software and configuration needed for the existing network management system (NMS) to create the STM-4 link that forms part of the Optic network from New Kilifi 220/132kV Substation and other Substation to the NCC/RCC/NSCC |  | Lot | 1
9.6 | Required equipment for PABX in RCC including all necessary Licenses, Network switches and any other facilities for communication with NCC,RCC and NSCC |  | Lot | 1
9.7 | Required equipment and accessories for interconnection between the OPGW and fibre optic cable in communication room
9.7.1 | Optical Distribution panel for Main Communication room |  | No | 1
9.7.2 | Optical Distribution Unit (OCDF) 48 cores fiber for Main Communication room |  | Set | 1
9.7.3 | Digital Distribution Unit (ODF) for 48 cores fiber |  | Set | 2
9.7.4 | Tail Optical Fiber |  | Lot | 1
9.7.5 | 48 cores Optical Cable |  | Lot | 1
9.7.6 | 2M Coaxial Cable |  | Lot | 1
9.7.7 | PVC Pipe suitable for the distance between entry gantry and communication room |  | Lot | 1
9.7.8 | Optical Cable plane |  | Lot | 1
9.7.9 | Steel Tube from junction box to entry of cable channel |  | Lot | 1
9.7.10 | OPGW Splice Closures joint box with all accessories |  | Set | 3
9.8 | EPABX system for communication between guard house and individual Staff housings including:
9.8.1 | Exchange |  | Lot | 1
9.8.2 | Telephone Equipment |  | No. | 16
9.8.3 | Junction Boxes |  | Lot | 1
9.8.4 | Cabling |  | Lot | 1
9.8.5 | Power supply with backup battery |  | Lot | 1
9.9 | VHF System included a station set and at least 4 portable handsets and batteries and battery chargers, suitable antenna with all accessories (RG, Heliax cabling, AC & DC cabling, indication lamp), supported tower with suitable height |  | Lot | 1
9.1 | Any other material for full functionality of the Telecommunication System |  | Lot. | 1
TOTAL PRICE ITEM 9
10 | LV CABLES AND ACCESSORIES
10.1 | Auxiliary power and control cabling including single and three phase power cables, control cables required for control; protection; metering and alarms, CT's and CVT's cabe circuits, DC supply cables. |  | Lot | 1
10.2 | Substation internal fibre optic cabling, coaxilal cables. |  | Lot | 1
10.3 | Cabling installation including, cable trays, ladders, supports & fixing calmps, accessories, glands, lugs, terminals, rails, labels, cable shoes, fire proof sealing of ducts/conduits/openings etc. |  | Lot | 1
TOTAL PRICE ITEM 10
11 | EARTHING & LIGHTNING PROTECTION AND LIGHTING SYSTEMS
11.1 | Earthing system (including main earth grid, earth mat, rizer, bonding, connector, clamp, fitting, earth rod and well, inspection earth pits etc. as required) |  | Lot | 1
11.2 | Lightning protection system (including shield wire, air termination rod, down conductor, equipotential bonding, disconnecting link, etc. as required) |  | Lot | 1
11.3 | Outdoor and indoor lighting, Emergency Lighting including the control building |  | Lot. | 1
TOTAL PRICE ITEM 11
12 | SUPPORT STRUCTURES
12.1 | Steel supports for 220kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
12.2 | Steel supports for 11kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
12.3 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
12.4 | Structures for interconnecting 220kV and 132kV switchyards bus (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
12.5 | Steel supports for 132kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
12.6 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
TOTAL PRICE ITEM 12
13 | AUXILIARY SUPPLY
13.1 | LVAC system
13.1.1 | AC Main and distribution panels, AC distribution outdoor cubicles, with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | Lot. | 1
13.1.2 | Oil treatment panel with fuse box socket and accessories (including heavy duty outlet socket, fuses, glands, etc.) |  | No. | 1
13.1.3 | Diesel Generator 250kVA including generator control and protection panel and all peripheral equipment, reservior(s), (foundations, structure), and accessories. |  | No. | 1
13.1.4 | Any other material for full functionality of the LVAC System |  | Lot. | 1
13.2 | LVDC system
13.2.1 | Supply, Installation, wiring, integration, test and commissioning of 110Vdc Main and distribution panels, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) as per 110Vdc SLD and Employer's Requirement |  | Lot | 1
13.2.2 | Supply, Installation, wiring,integration, test and commissioning of 48Vdc distribution panel, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) as per 48Vdc SLD and Epmployer's Requirement |  | Lot | 1
13.3.3 | Any other material for full functionality of the LVDC System |  | Lot. | 1
13.4.4 | 415V ac Uninterruptible Power Supply including isolating by-pass transformers, inverters, static switch, manual bypass switch, panels & distribution boards as per SLD and Epmployer's Requirement |  | Set | 2
13.5 | 400Ah battery bank (Ni-Cd) Batteries |  | Nos. | 2
13.6 | 100A Float cum boost charger |  | Nos. | 2
TOTAL PRICE ITEM 13
14 | TARIFF METERING
14.1 | Tariff metering System for 220kV OHL, complete with wiring, accessories and etc. including:
14.1.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy |  | No. | 2
14.1.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy |  | No. | 2
14.2 | Tariff metering System for Power Transformer, complete with wiring, accessories etc. and including (on 220kV side):
14.2.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy |  | No. | 2
14.2.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy |  | No. | 2
14.3 | Metering data collection and communication system, complete with fibre optic cabling, accessories, Each kind of energy meters software and communication ports. All media and accessories in order to transferring Energy meter measuring values to remote center according to both KETRACO and KPLC required specification. |  | Lot | 1
14.4 | Metering panel with all accessories and auxiliaries, lighting, heating, socket, wiring, terminals, test facilities, and all other switches, labels, test block/plug , Labels, etc. |  | No. | 2
14.5 | All other related relays, racks, Voltage/Current test block, cubicles, terminals, As needed to complete the metering system. |  | Lot | 1
TOTAL PRICE ITEM 14
15 | MISCELLANEOUS
15.1 | Required Bay Marshalling Kiosk |  | Lot. | 1
15.2 | CCTV System with all ralated equipment for indoor and outdoor, including Cameras of suitable type and required specifications with poles, recorder, storage, monitor, switch, cabling, boxes, fixings, brackets and etc. (acc. to technical specifications in part 2-B) |  | Lot | 1
15.3 | Padlocks / Keys (for panels, outdoor equipments, doors, etc.) |  | Lot | 1
15.4 | Equipment/Bay labels, safety warning plates, road signages, room name plates, etc. |  | Lot | 1
15.5 | Tools and Appliances as stated in Clause 20 of Part 2-A of the Employer's Requirements |  | Lot | 1
15.6 | Tools and Equipment for Erection, Installation, Commissioning and Operation as stated in part 2-A, Clause 21 of the Employers Requirements |  | Lot | 1
15.6.1 | Special tools and equipment
15.6.1.1 | Multi-ammeter (clamp type) |  | No | 1
15.6.1.2 | Megger with 1/2/5/10 kV |  | No | 1
15.6.1.3 | Digital ground resistance measuring test set |  | No | 1
15.6.1.4 | Test plugs of protection system |  | No | 1
15.6.1.5 | Thermometer, density meter, tools for battery filling and fuse puller for each substation |  | Set | 1
15.6.1.6 | Thermo-vision camera |  | No | 1
15.6.1.7 | Digital camera |  | No | 1
15.6.1.8 | Walkie-talkie (2 pairs) |  | Set | 2
15.6.1.9 | Gas handling trolley (complete set), |  | Set | 1
15.6.1.10 | Portable Earth Leads for each voltage level |  | Set | 1
15.6.1.11 | Forklift, 1 set for New Kilifi storage warehouse |  | Set | 1
15.6.1.12 | Aluminium ladder |  | Set | 1
15.6.1.13 | Warning signs and boards |  | Set | 1
15.6.1.14 | Articulating Boom Lift for Substation Maintenance |  | Set | 1
15.6.1.15 | CMC-500 |  | Set | 1
15.6.2 | Project Laptops with all required software as per Client's requirmenets in Part 2-A, clause 21 |  | No. | 4
15.6.3 | Rugged/Industrial Laptop for substation protection and control system (CRP/SAS) with all required softwareas, as per Client's requirmenets in Part 2-A, clause 21 |  | No. | 1
15.6.4 | Laptop tablets as per Client Requirements in Part 2-A, clause 21 |  | No | 2
15.6.5 | Control System Printers
15.6.5.1 | SOE Printer |  | No | 1
15.6.5.2 | Station Log Printer |  | No | 1
15.6.5.3 | General Purpose Printer |  | No | 1
15.6.6 | Software
15.6.6.1 | Server based licenses (where available) and subscriptions, six user licenses for a period of six years. |  | Lot | 1
15.6.6.2 | software including but not limited to Anti-Virus Software, Microsoft Office Latest, BCU Interface and Configuration Software, HMI Server/Client and Configuration Software License |  | Lot | 1
15.7 | Salt water filter machine with all accessories connected to the main tank |  | No | 1
15.8 | Mobile telephone sets per substation as specified in Employers Requirement (smart phone, approved by the Employer) |  | No | 10
15.9 | Satellite phones as specified in employers requirement (satellite phone, approved by the Employer) |  | No. | 5
15.10 | Environmental and Social Equipment requirements
15.10.1 | Portable multi-parameter water meters-HACC MP-6p Portable Meter |  | No | 2
15.10.2 | Portable data Loggers for ambient Temp & Humidity- Lascar Temperature & Humidity Data Logger |  | No | 2
15.10.3 | Binoculars- K&F Concept 20×50 High Power Binoculars- |  | No | 2
15.10.4 | Velocity Meters- Scarlet WR3 Anemometer |  | No | 2
15.10.5 | EMF meters- Extech 480836 RF EM |  | No | 2
15.10.6 | Noise/Sound meters. - Reed R8050 Sound Level Meter |  | No | 2
15.10.7 | Bosch GLM 50-27 CG Laser Distance Meter |  | No | 2
15.11 | 50 Mbps symmetric internet bandwidth in the control room building and in the regional office separately for scalable and future-proof connectivity to support basic IT Functions (Email, ERP access, VoIP, Patch Management) and Video Surveillance Streaming and Remote Support Capabilities . Design should allow easy upgrades of bandwidth and hardware as needs evolve. |  | Lot | 1
15.12 | Any other items not included above but required to complete the project successfully. (Tenderer shall specify and include breakdown of price in his proposal) |  | Lot | 1
TOTAL PRICE ITEM 15
16 | SITE TRANSPORT and SITE OFFICE Provision as per Employer's Requirements, Clause 27 & 28 of Part 2-A of Employer's Requirements
16.1 | Vehicles as per part 2-A, Clause 28
16.1.1 | Vehicle Type 1 |  | No. | 4
16.1.2 | Vehicle Type 2 |  | No | 2
TOTAL PRICE ITEM 16
MANDATORY SPARES
17 | 220kV & 132kV PRIMARY PLANT
17.1 | 220kV & 132 kV Circuit Breaker (3-phase)
17.1.1 | 220kV & 132 kV Circuit Breaker (3-phase) (for each CB)
17.1.2 | Trip coil |  | No. | 1
17.1.3 | Closing coil |  | No. | 1
17.1.4 | Anti pumping relay |  | No. | 1
17.1.5 | Density blocking relay |  | No. | 1
17.1.6 | Density meter |  | No. | 1
17.1.7 | Heater |  | No. | 1
17.1.8 | Motor for operating mechanism |  | No. | 1
17.1.9 | Complete pole including fixed and moving contacts, pull rod, etc. |  | No. | 1
17.1.9 | Relevant Peripheral Devices/ Material
17.1.10 | Gas filling devices |  | No. | 1
17.1.11 | SF6 gas |  | Kg | 20% of required volume for first filling of CBs
17.2 | SF6 gas leakage detector |  | No. | 1
17.2.1 | Motorized disconnector (3-phase), complete with one integral motorised earth switch, and earth mat (for each 220kV & 132kV voltage)
17.2.2 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-ES (3-phase) |  | No. | 1
17.3 | Motorized operating mechanism suitable for DS-ES |  | No. | 1
17.3.1 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 1
17.3.2 | Post insulator of all types |  | % | 0.1
17.4 | Insulator string of all types (suspension and strain types with hardware fitting) |  | % | 0.1
17.4.1 | Post type current transformer, for protection and metering, six cores (1-phase) |  | No. | 1
17.4.2 | Capacitive voltage transformer protection and metering three cores (1-phase) |  | No. | 1
17.5 | Conductor - Stranded of all types |  | drum | 1
17.6 | Connectors and clamps for tubular conductors of all types (together with stainless steel nuts, bolts, bimetal) |  | No. | 3
17.7 | Connectors and clamps for stranded conductors of all types(together with stainless steel nuts, bolts, bimetal) |  | No. | 3
17.8 | Post type current transformer, for protection and metering, six cores (1-phase) |  | No. | 1
17.9 | Post type current transformer, for protection and metering, five cores (1-phase) |  | No. | 1
17.1 | Post type current transformer, for protection and measuring, four cores (1-phase) |  | No. | 1
17.11 | Post type current transformer, for protection, two cores (1-phase) |  | No. | 1
17.12 | Capacitive voltage transformer protection and metering three cores (1-phase) |  | No. | 1
17.13 | Capacitive voltage transformer protection and measuring two cores (1-phase) |  | No. | 1
17.14 | Conductor - Tubular of all types |  | % | 0.1
17.15 | Conductor - Stranded of all types |  | % | 0.1
17.16 | Connectors and clamps for tubular conductors of all types (together with stainless steel nuts, bolts, bimetal) |  | % | 0.1
17.17 | Connectors and clamps for stranded conductors of all types(together with stainless steel nuts, bolts, bimetal) |  | % | 0.1
TOTAL PRICE ITEM 17_Spares
18 | POWER TRANSFORMER (P.TR.)
18.1 | Power transformer three phase units HV220/MV 132/LV11kV, 90-110MVA including HV/LV/Neutral Bushing CT's, OLTC, RTCC, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS
18.1.1 | Bushing for HV side |  | No. | 1
18.1.2 | Bushing for LV side |  | No. | 1
18.1.3 | Bushing for Neutral LV side |  | No. | 1
18.1.4 | Oil directed pressure relief device (main tank) |  | No. | 1
18.1.5 | Oil directed pressure relief device (OLTC) |  | No. | 1
18.1.6 | Buchholz relay |  | No. | 1
18.1.7 | Oil Level Indicator for main tank |  | No. | 1
18.1.8 | Oil level indicator for OLTC |  | No. | 1
18.1.9 | Oil surge relay for OLTC |  | No. | 1
18.1.10 | Cooling fan |  | No. | 4
18.1.11 | Winding temperature indicator |  | No. | 1
18.1.12 | Oil temperature indicator |  | No. | 1
18.1.13 | Valves for radiators |  | Set | 1
18.1.14 | Contactors and required accessories eg. Aux. Relay, MCB, Control relay, and etc. (in Marshalling Kiosk) |  | No. | 1
18.1.15 | Transducer of each type |  | Set | 1
18.1.16 | Pre-stressed non-return valve (PNRV) |  | No. | 1
18.1.17 | Complete set of gaskets |  | Set | 1
TOTAL PRICE ITEM 18_Spares
Relevant Peripheral Material
19.1.18 | Transformer oil |  | Drum | 10% of total transformer oil volume
19.1.19 | Silicagel |  | Kg | Equal to the quantity of the first filling
TOTAL PRICE ITEM 19_Spares
20 | 220kV & 132kV PROTECTION SYSTEMS- For each voltage class
20.1 | 220kV & 132kV OHL Protection System (for each voltage class)
20.1.1 | Main 1 21L Protection(with all required functions as per PSLD) |  | No. | 1
20.1.2 | Main 2 87L Protection(with all required functions as per PSLD) |  | No. | 1
20.1.3 | Trip circuit supervison relay; |  | No. | 3
20.1.4 | Lockout relay; |  | No. | 3
21.2 | Transformer 220kV & 132kV Side Protection System including:
20.2.1 | Main 87T+87NT Protection(with all required functions as per PSLD) |  | No. | 1
20.2.2 | Backup 67/67(N) Protection(with all required functions as per PSLD) |  | No. | 1
20.2.3 | Tripcircuit supervison relay; |  | No. | 1
20.2.4 | Lockout relay; |  | No. | 1
20.3 | Completion and Modification of 132kV Low Impedance Type Busbar Protection System
20.3.1 | Trip Relay |  | No. | 1
TOTAL PRICE ITEM 20-Spares
21 | 220/132kV SUBSTATION CONTROL SYSTEM
21.1 | Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) |  | Lot | 1
TOTAL PRICE ITEM 21_Spares
22 | AUXILIARY SUPPLY
TOTAL PRICE ITEM 22_Spares
TOTAL PRICE SCHEDULE 1 NEW KILIFI SUBSTATION Note: Contractor shall include all equipment and materials in his proposal, which are necessary to complete the works.
TOTAL PRICE SCHEDULE 1 NEW KILIFI SUBSTATION_Spare Parts

## Schedule_2_SS
SCHEDULE NO. 2
PLANT, EQUIPMENT AND MANDATORY SPARE PARTS SUPPLIED FROM WITHIN THE EMPLOYER'S COUNTRY
FOR NEW KILIFI SUBSTATION
Note 1: All proposed mandatory spare parts for each equipment or system shall be specified in detail by Bidders.
Note 2: All main and spare equipment shall be provided for proper operation in 1000m altitude. In case of other range may has been mentioned in the schedules of technical information (Part 2-E), the higher altitude category shall be considered.
Note 3: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
1 | 2 | 2 | 3 | 4 | 5
Item No | Description | Unit | Estimated Quantity | Local Currency (Ksh) = KENYAN SHILLINGS | Total Price (Ksh)
|  |  |  | Local Manufacture | Local Manufacture
|  |  |  | Unit Price (DAP) | (Quantity x Unit Price)
EQUIPMENT AND MATERIAL
1 | 220kV PRIMARY PLANT
1.1 | 220kV Circuit Breaker (3 phase) 2500A, 40kA - single pole | No. | 6
1.2 | Motorized disconnector (3-phase) 220kV,2500A,40kA, with two (2) earthing switch with earth mat | Set | 4
1.3 | Motorized disconnector (3-phase) 220kV,2500A,40kA, with one (1) earthing switch, and earth mat | Set | 12
1.4 | 220kV, 40kA Motorized earthing switch (3-phase) with earth mat | Set | 2
1.5 | Surge arrester 220kV (1-phase) including surge counter and earth leakage meter | No. | 12
1.6 | Post Insulator | Lot | 1
1.7 | Insulator string (suspension and strain types with hardware fitting) | Lot | 1
1.8 | 220 kV Post type current transformer, for protection and metering, five cores (1-phase) | No. | 18
1.9 | 220 kV Post type current transformer, for metering, two cores (1-phase) | No. | 6
1.10 | 220 kV Capacitive voltage transformer protection and metering three cores (1-phase) | No. | 6
1.11 | 132 kV Capacitive voltage transformer protection and measuring two cores (1-phase) | No. | 18
1.12 | Conductor - Tubular | Lot | 1
1.13 | Conductor - Stranded | Lot | 1
1.14 | Connectors and clamps for tubular conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
1.15 | Connectors and clamps for stranded conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
TOTAL PRICE ITEM 1
2 | 132kV PRIMARY PLANT
2.1 | 132kV Circuit Breaker (3 phase) 1250A, 31.5kA | Set. | 3
2.2 | Motorized disconnector (3-phase), without earth switch, with earth mat | Set | 6
2.3 | Motorized disconnector (3-phase), complete with one integral motorised earth switch, and earth mat | Set | 2
1.6 | 132kV, 31.5kA Motorized earthing switch (3-phase) with earth mat | Set | 2
2.4 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 6
2.5 | Post insulator | Lot | 1
2.6 | Insulator string (suspension and strain types with hardware fitting) | Lot | 1
2.7 | Post type current transformer protection and metering five cores (1-phase) | No. | 3
2.8 | Post type current transformer, for protection, four cores (1-phase) | No. | 6
2.9 | Post type current transformer, for protection,two cores (1-phase) | No. | 6
2.9 | Voltage transformer Protection and metering Two Cores (1-phase) | No. | 6
2.10 | Conductor - Stranded | Lot | 1
2.11 | Connectors and clamps for stranded conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
TOTAL PRICE ITEM 2
3 | AUTOTRANSFORMER (A.TR.)
3.1 | Autotransformer three phase units HV220/MV132/TV11kV, 90-110MVA including HV/MV/TV/Neutral Bushing CT's, OLTC, RTCC, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS | No. | 2
3.2 | Fire Detection and Protection System (Nitrogen Injection system) | Lot | 2
3.3 | 50 kg wheeled Dry-Powder Fire extinguisher for Power Transformer | No. | 2
TOTAL PRICE ITEM 3
4 | EARTHING & AUXILIARY TRANSFORMER
4.1 | 11/0.415kV, 500kVA, ZNyn11 Earthing & Auxiliary transformers including all accessories as required | No. | 2
4.2 | 11kV, 30A 3-phase cut off fuse | No. | 6
4.3 | 50 kg wheeled Dry-Powder Fire extinguisher for Auxiliary transformer | No. | 2
4.4 | 500A/10s Neutral Earthing Resistor (NER) including all accessories as required | No. | 2
TOTAL PRICE ITEM 4
5 | 220kV & 132 PROTECTION SYSTEMS
5.1 | 220kV Diameter (OHL) Protection System including:
5.1.1 | Main 1 21L Protection(with all required functions as per PSLD) | No. | 2
5.1.2 | Main 2 87L Protection(with all required functions as per PSLD) | No. | 2
5.1.3 | 87T/87NT protection with all required functions as per PSLD | No. | 2
5.1.4 | 87HVC protection with all required functions as per PSLD | No. | 2
5.1.5 | Auto-Reclose Protection Relay(with all required functions and Voltage Selection Logic as per PSLD) | No. | 2
5.1.6 | All other relays or functions such as over voltage; under voltage; trip relay; trip circuit supervison; pole discordance; synchro check; fuse failure; close relay; lockout relay; short zone, end zone; circuit breaker failure, cubicles, test blocks and test plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the full protection scheme. | Lot | 1
5.1.7 | Panels including all accessories ACC the PSLD, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 12
5.1.8 | Equipment for modification works in remote existing Malindi, substation including name tags, differential relays settings and etc.. | Lot | 1
5.2 | Transformer 132kV Side and Neutral Earthing Transformer Protection System including:
5.2.1 | Main 87LVC Protection(with all required functions as per PSLD) | No. | 2
5.2.2 | Backup 67/67(N) Protection(with all required functions as per PSLD) | No. | 2
5.2.3 | Earth Fault 50N/51N (SBEF) Protection (with all required functions as per PSLD) | No. | 2
5.2.4 | 50TV protection with all required functions as per PSLD | No. | 2
5.2.5 | 87NTV protection with all required functions as per PSLD | No. | 2
5.2.6 | All other relays or functions such as over voltage; under voltage; trip relay; trip circuit supervison; pole discordance; synchro check; fuse failure; close relay; lockout relay; short zone, end zone; circuit breaker failure, cubicles, test blocks and test plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the full protection scheme. | Lot | 1
5.2.7 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 5
5.3 | 220kV & 132kV Busbar Protection System
5.3.1 | 220kV Busbar Protection System
5.3.1.1 | 220kV Low Impedance type Busbar Protection Relay ACC. To PSLD drawing and considering future extension | No. | 2
5.3.1.2 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux relays, test and terminal blocks, timers, wiring etc. to make the system complete | No. | 2
5.3.2 | 132kV Busbar Protection System
5.3.2.1 | 132kV Low Impedance type Busbar Protection Relay ACC. To PSLD drawing and considering future extension | No. | 2
5.3.2.2 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux relays, test and terminal blocks, timers, wiring etc. to make the system complete | No. | 2
5.4 | Miscellaneous modification works as necessary to make a complete functional 220 &132kV protection system | Lot | 1
TOTAL PRICE ITEM 5
6 | AVR PROTECTION SYSTEMS
6.2 | Autotransformer Automatic Voltage Regulation System including:
6.2.1 | Automatic Voltage Regulator Relay (AVR) | No. | 2
6.2.2 | Panels with all accessories and auxiliaries, lighting, heating, socket, push buttons, wiring, terminals, test facilities, discrepancy and all other switches, labels, unit measurement indicating lamps, position indicators, alarm announciators, temperature indicators, test block/plug , Labels, etc. and with the following equipment. | No. | 2
TOTAL PRICE ITEM 6
7 | 220/132kV SUBSTATION CONTROL SYSTEM
7.1 | Substation automation system including:
7.1.1 | All software and license, Modifications in HMI | Lot | 1
7.1.2 | Bay Control and Protection Units (BCU/BCPU)(with all required functions as per PSLD) | No. | 6
7.1.3 | Bay Control Panels | No. | 2
7.1.4 | Auxiliary and Common Services Bay Control Unit | Lot | 1
7.1.5 | Auxiliary and Common Services Panel including all accessories | Lot | 1
7.1.6 | Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
7.1.7 | Human Machine Interface Systems and Computers | No. | 2
7.1.8 | Any other material for full functionality of the Substation Control System | Lot. | 1
7.1.9 | Fault Monitoring System and Alarm System | Lot | 1
8 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
8.1 | Equipment for Modification works at Remote SS | Lot | 1
9 | TELECOMMUNICATION & NCC/RCC/NSCC
9.1 | Required equipment for Telecommunication and Teleprotection Signalling System | Lot | 1
9.1.1 | Required equipment for Telecommunication SDH System | Lot | 1
9.1.2 | Required equipment for Teleprotection Signalling Equipment Interface Board for Distance & Differential protection relay | Lot | 1
9.2 | New Firewall system with all necessary Licenses | Lot | 1
9.3 | Required equipment for incorporating substation equipment into the SCADA/EMS System at the NCC/RCC/NSCC | Lot | 1
9.4 | Required equipment for modifications to NCC/RCC/NSCC mimic board (if any) | Lot | 1
9.5 | All necessary licences, hardware, software and configuration needed for the existing network management system (NMS) to create the STM-4 link that forms part of the Optic network from New Kilifi 220/132kV Substation and other Substation to the NCC/RCC/NSCC | Lot | 1
9.6 | Required equipment for PABX in RCC including all necessary Licenses, Network switches and any other facilities for communication with NCC,RCC and NSCC | Lot | 1
9.7 | Required equipment and accessories for interconnection between the OPGW and fibre optic cable in communication room
9.7.1 | Optical Distribution panel for Main Communication room | No | 1
9.7.2 | Optical Distribution Unit (OCDF) 48 cores fiber for Main Communication room | Set | 1
9.7.3 | Digital Distribution Unit (ODF) for 48 cores fiber | Set | 2
9.7.4 | Tail Optical Fiber | Lot | 1
9.7.5 | 48 cores Optical Cable | Lot | 1
9.7.6 | 2M Coaxial Cable | Lot | 1
9.7.7 | PVC Pipe suitable for the distance between entry gantry and communication room | Lot | 1
9.7.8 | Optical Cable plane | Lot | 1
9.7.9 | Steel Tube from junction box to entry of cable channel | Lot | 1
9.7.10 | OPGW Splice Closures joint box with all accessories | Set | 3
9.8 | EPABX system for communication between guard house and individual Staff housings including:
9.8.1 | Exchange | Lot | 1
9.8.2 | Telephone Equipment | No. | 16
9.8.3 | Junction Boxes | Lot | 1
9.8.4 | Cabling | Lot | 1
9.8.5 | Power supply with backup battery | Lot | 1
9.9 | VHF System included a station set and at least 4 portable handsets and batteries and battery chargers, suitable antenna with all accessories (RG, Heliax cabling, AC & DC cabling, indication lamp), supported tower with suitable height | Lot | 1
9.1 | Any other material for full functionality of the Telecommunication System | Lot. | 1
TOTAL PRICE ITEM 9
10 | LV CABLES AND ACCESSORIES
10.1 | Auxiliary power and control cabling including single and three phase power cables, control cables required for control; protection; metering and alarms, CT's and CVT's cabe circuits, DC supply cables. | Lot | 1
10.2 | Substation internal fibre optic cabling, coaxilal cables. | Lot | 1
10.3 | Cabling installation including, cable trays, ladders, supports & fixing calmps, accessories, glands, lugs, terminals, rails, labels, cable shoes, fire proof sealing of ducts/conduits/openings etc. | Lot | 1
TOTAL PRICE ITEM 10
11 | EARTHING & LIGHTNING PROTECTION AND LIGHTING SYSTEMS
11.1 | Earthing system (including main earth grid, earth mat, rizer, bonding, connector, clamp, fitting, earth rod and well, inspection earth pits etc. as required) | Lot | 1
11.2 | Lightning protection system (including shield wire, air termination rod, down conductor, equipotential bonding, disconnecting link, etc. as required) | Lot | 1
11.3 | Outdoor and indoor lighting, Emergency Lighting including the control building | Lot. | 1
TOTAL PRICE ITEM 11
12 | SUPPORT STRUCTURES
12.1 | Steel supports for 220kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.2 | Steel supports for 11kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.3 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.4 | Structures for interconnecting 220kV and 132kV switchyards bus (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.5 | Steel supports for 132kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.6 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
TOTAL PRICE ITEM 12
13 | AUXILIARY SUPPLY
13.1 | LVAC system
13.1.1 | AC Main and distribution panels, AC distribution outdoor cubicles, with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | Lot. | 1
13.1.2 | Oil treatment panel with fuse box socket and accessories (including heavy duty outlet socket, fuses, glands, etc.) | No. | 1
13.1.3 | Diesel Generator 250kVA including generator control and protection panel and all peripheral equipment, reservior(s), (foundations, structure), and accessories. | No. | 1
13.1.4 | Any other material for full functionality of the LVAC System | Lot. | 1
13.2 | LVDC system
13.2.1 | Supply, Installation, wiring, integration, test and commissioning of 110Vdc Main and distribution panels, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) as per 110Vdc SLD and Employer's Requirement | Lot | 1
13.2.2 | Supply, Installation, wiring,integration, test and commissioning of 48Vdc distribution panel, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) as per 48Vdc SLD and Epmployer's Requirement | Lot | 1
13.3 | Any other material for full functionality of the LVDC System | Lot. | 1
13.4 | 415V ac Uninterruptible Power Supply including isolating by-pass transformers, inverters, static switch, manual bypass switch, panels & distribution boards as per SLD and Epmployer's Requirement | Set | 2
13.5 | 400Ah battery bank (Ni-Cd) Batteries | Nos. | 2
13.6 | 100A Float cum boost charger | Nos. | 2
TOTAL PRICE ITEM 13
14 | TARIFF METERING
14.1 | Tariff metering System for 220kV OHL, complete with wiring, accessories and etc. including:
14.1.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
14.1.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
14.2 | Tariff metering System for Power Transformer, complete with wiring, accessories etc. and including (on 220kV side):
14.2.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
14.2.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
14.3 | Metering data collection and communication system, complete with fibre optic cabling, accessories, Each kind of energy meters software and communication ports. All media and accessories in order to transferring Energy meter measuring values to remote center according to both KETRACO and KPLC required specification. | Lot | 1
14.4 | Metering panel with all accessories and auxiliaries, lighting, heating, socket, wiring, terminals, test facilities, and all other switches, labels, test block/plug , Labels, etc. | No. | 2
14.5 | All other related relays, racks, Voltage/Current test block, cubicles, terminals, As needed to complete the metering system. | Lot | 1
TOTAL PRICE ITEM 14
15 | MISCELLANEOUS
15.1 | Required Bay Marshalling Kiosk | Lot. | 1
15.2 | CCTV System with all ralated equipment for indoor and outdoor, including Cameras of suitable type and required specifications with poles, recorder, storage, monitor, switch, cabling, boxes, fixings, brackets and etc. (acc. to technical specifications in part 2-B) | Lot | 1
15.3 | Padlocks / Keys (for panels, outdoor equipments, doors, etc.) | Lot | 1
15.4 | Equipment/Bay labels, safety warning plates, road signages, room name plates, etc. | Lot | 1
15.5 | Tools and Appliances as stated in Clause 20 of Part 2-A of the Employer's Requirements | Lot | 1
15.6 | Tools and Equipment for Erection, Installation, Commissioning and Operation as stated in part 2-A, Clause 21 of the Employers Requirements | Lot | 1
15.6.1 | Special tools and equipment
15.6.1.1 | Multi-ammeter (clamp type) | No | 1
15.6.1.2 | Megger with 1/2/5/10 kV | No | 1
15.6.1.3 | Digital ground resistance measuring test set | No | 1
15.6.1.4 | Test plugs of protection system | No | 1
15.6.1.5 | Thermometer, density meter, tools for battery filling and fuse puller for each substation | Set | 1
15.6.1.6 | Thermo-vision camera | No | 1
15.6.1.7 | Digital camera | No | 1
15.6.1.8 | Walkie-talkie (2 pairs) | Set | 2
15.6.1.9 | Gas handling trolley (complete set), | Set | 1
15.6.1.10 | Portable Earth Leads for each voltage level | Set | 1
15.6.1.11 | Forklift, 1 set for New Kilifi storage warehouse | Set | 1
15.6.1.12 | Aluminium ladder | Set | 1
15.6.1.13 | Warning signs and boards | Set | 1
15.6.1.14 | Articulating Boom Lift for Substation Maintenance | Set | 1
15.6.1.15 | CMC-500 | Set | 1
15.6.2 | Project Laptops with all required software as per Client's requirmenets in Part 2-A, clause 21 | No. | 4
15.6.3 | Rugged/Industrial Laptop for substation protection and control system (CRP/SAS) with all required softwareas, as per Client's requirmenets in Part 2-A, clause 21 | No. | 1
15.6.4 | Laptop tablets as per Client Requirements in Part 2-A, clause 21 | No | 2
15.6.5 | Control System Printers
15.6.5.1 | SOE Printer | No | 1
15.6.5.2 | Station Log Printer | No | 1
15.6.5.3 | General Purpose Printer | No | 1
15.6.6 | Software
15.6.6.1 | Server based licenses (where available) and subscriptions, six user licenses for a period of six years. | Lot | 1
15.6.6.2 | software including but not limited to Anti-Virus Software, Microsoft Office Latest, BCU Interface and Configuration Software, HMI Server/Client and Configuration Software License | Lot | 1
15.7 | Salt water filter machine with all accessories connected to the main tank | No | 1
15.8 | Mobile telephone sets per substation as specified in Employers Requirement (smart phone, approved by the Employer) | No | 10
15.9 | Satellite phones as specified in employers requirement (satellite phone, approved by the Employer) | No. | 5
15.10 | Environmental and Social Equipment requirements
15.10.1 | Portable multi-parameter water meters-HACC MP-6p Portable Meter | No | 2
15.10.2 | Portable data Loggers for ambient Temp & Humidity- Lascar Temperature & Humidity Data Logger | No | 2
15.10.3 | Binoculars- K&F Concept 20×50 High Power Binoculars- | No | 2
15.10.4 | Velocity Meters- Scarlet WR3 Anemometer | No | 2
15.10.5 | EMF meters- Extech 480836 RF EM | No | 2
15.10.6 | Noise/Sound meters. - Reed R8050 Sound Level Meter | No | 2
15.10.7 | Bosch GLM 50-27 CG Laser Distance Meter | No | 2
15.11 | 50 Mbps symmetric internet bandwidth in the control room building and in the regional office separately for scalable and future-proof connectivity to support basic IT Functions (Email, ERP access, VoIP, Patch Management) and Video Surveillance Streaming and Remote Support Capabilities . Design should allow easy upgrades of bandwidth and hardware as needs evolve. | Lot | 1
15.12 | Any other items not included above but required to complete the project successfully. (Tenderer shall specify and include breakdown of price in his proposal) | Lot | 1
TOTAL PRICE ITEM 15
16 | SITE TRANSPORT and SITE OFFICE Provision as per Employer's Requirements, Clause 27 & 28 of Part 2-A of Employer's Requirements
16.1 | Vehicles as per part 2-A, Clause 28
16.1.1 | Vehicle Type 1 | No. | 4
16.1.2 | Vehicle Type 2 | No | 2
TOTAL PRICE ITEM 16
MANDATORY SPARES
17 | 220kV & 132kV PRIMARY PLANT
17.1 | 220kV & 132 kV Circuit Breaker (3-phase)
17.1.1 | 220kV & 132 kV Circuit Breaker (3-phase) (for each CB)
17.1.2 | Trip coil | No. | 1
17.1.3 | Closing coil | No. | 1
17.1.4 | Anti pumping relay | No. | 1
17.1.5 | Density blocking relay | No. | 1
17.1.6 | Density meter | No. | 1
17.1.7 | Heater | No. | 1
17.1.8 | Motor for operating mechanism | No. | 1
17.1.9 | Complete pole including fixed and moving contacts, pull rod, etc. | No. | 1
17.1.9 | Relevant Peripheral Devices/ Material
17.1.10 | Gas filling devices | No. | 1
17.1.11 | SF6 gas | Kg | 20% of required volume for first filling of CBs
17.2 | SF6 gas leakage detector | No. | 1
17.2.1 | Motorized disconnector (3-phase), complete with one integral motorised earth switch, and earth mat (for each 220kV & 132kV voltage)
17.2.2 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-ES (3-phase) | No. | 1
17.3 | Motorized operating mechanism suitable for DS-ES | No. | 1
17.3.1 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 1
17.3.2 | Post insulator of all types | % | 0.1
17.4 | Insulator string of all types (suspension and strain types with hardware fitting) | % | 0.1
17.4.1 | Post type current transformer, for protection and metering, six cores (1-phase) | No. | 1
17.4.2 | Capacitive voltage transformer protection and metering three cores (1-phase) | No. | 1
17.5 | Conductor - Stranded of all types | drum | 1
17.6 | Connectors and clamps for tubular conductors of all types (together with stainless steel nuts, bolts, bimetal) | No. | 3
17.7 | Connectors and clamps for stranded conductors of all types(together with stainless steel nuts, bolts, bimetal) | No. | 3
17.8 | Post type current transformer, for protection and metering, six cores (1-phase) | No. | 1
17.9 | Post type current transformer, for protection and metering, five cores (1-phase) | No. | 1
17.1 | Post type current transformer, for protection and measuring, four cores (1-phase) | No. | 1
17.11 | Post type current transformer, for protection, two cores (1-phase) | No. | 1
17.12 | Capacitive voltage transformer protection and metering three cores (1-phase) | No. | 1
17.13 | Capacitive voltage transformer protection and measuring two cores (1-phase) | No. | 1
17.14 | Conductor - Tubular of all types | % | 0.1
17.15 | Conductor - Stranded of all types | % | 0.1
17.16 | Connectors and clamps for tubular conductors of all types (together with stainless steel nuts, bolts, bimetal) | % | 0.1
17.17 | Connectors and clamps for stranded conductors of all types(together with stainless steel nuts, bolts, bimetal) | % | 0.1
TOTAL PRICE ITEM 17_Spares
18 | POWER TRANSFORMER (P.TR.)
18.1 | Power transformer three phase units HV220/MV 132/LV11kV, 90-110MVA including HV/LV/Neutral Bushing CT's, OLTC, RTCC, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS
18.1.1 | Bushing for HV side | No. | 1
18.1.2 | Bushing for LV side | No. | 1
18.1.3 | Bushing for Neutral LV side | No. | 1
18.1.4 | Oil directed pressure relief device (main tank) | No. | 1
18.1.5 | Oil directed pressure relief device (OLTC) | No. | 1
18.1.6 | Buchholz relay | No. | 1
18.1.7 | Oil Level Indicator for main tank | No. | 1
18.1.8 | Oil level indicator for OLTC | No. | 1
18.1.9 | Oil surge relay for OLTC | No. | 1
18.1.10 | Cooling fan | No. | 4
18.1.11 | Winding temperature indicator | No. | 1
18.1.12 | Oil temperature indicator | No. | 1
18.1.13 | Valves for radiators | Set | 1
18.1.14 | Contactors and required accessories eg. Aux. Relay, MCB, Control relay, and etc. (in Marshalling Kiosk) | No. | 1
18.1.15 | Transducer of each type | Set | 1
18.1.16 | Pre-stressed non-return valve (PNRV) | No. | 1
18.1.17 | Complete set of gaskets | Set | 1
TOTAL PRICE ITEM 18_Spares
Relevant Peripheral Material
19.1.18 | Transformer oil | Drum | 10% of total transformer oil volume
19.1.19 | Silicagel | Kg | Equal to the quantity of the first filling
TOTAL PRICE ITEM 19_Spares
20 | 220kV & 132kV PROTECTION SYSTEMS- For each voltage class
20.1 | 220kV & 132kV OHL Protection System (for each voltage class)
20.1.1 | Main 1 21L Protection(with all required functions as per PSLD) | No. | 1
20.1.2 | Main 2 87L Protection(with all required functions as per PSLD) | No. | 1
20.1.3 | Trip circuit supervison relay; | No. | 3
20.1.4 | Lockout relay; | No. | 3
21.2 | Transformer 220kV & 132kV Side Protection System including:
20.2.1 | Main 87T+87NT Protection(with all required functions as per PSLD) | No. | 1
20.2.2 | Backup 67/67(N) Protection(with all required functions as per PSLD) | No. | 1
20.2.3 | Tripcircuit supervison relay; | No. | 1
20.2.4 | Lockout relay; | No. | 1
20.3 | Completion and Modification of 132kV Low Impedance Type Busbar Protection System
20.3.1 | Trip Relay | No. | 1
TOTAL PRICE ITEM 20-Spares
21 | 220/132kV SUBSTATION CONTROL SYSTEM
21.1 | Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
TOTAL PRICE ITEM 21_Spares
22 | AUXILIARY SUPPLY
TOTAL PRICE ITEM 22_Spares
TOTAL PRICE SCHEDULE 2 NEW KILIFI SUBSTATION Note: Contractor shall include all equipment and materials in his proposal, which are necessary to complete the works.
TOTAL PRICE SCHEDULE 2 NEW KILIFI SUBSTATION_Spare Parts

## Schedule_3_SS
SCHEDULE NO. 3
DESIGN SERVICES
FOR NEW KILIFI SUBSTATION
Note 1: All of the manufacturer's documentations including test reports, layout and dimensions drawings, datasheets, Catalogs, O&M instruction manuals, etc. shall be submitted to the Client.
Note 2: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Item No | Description | Unit | Estimated Quantity | Foreign Currency (FC1) = USD (FC2) = EURO |  | Local Currency (KSh) = KENYAN SHILLINGS | Total Price
[5 empty] | Design Services |  | Design Services | Design Services
[5 empty] | Unit Price |  | Unit Price | (Quantity x Unit Price)
[5 empty] | FC1 | FC2 | KSh | FC1 | FC2 | KSh
| 1 | DESIGN SERVICES
| 1.1 | 220kV and 132kV primary equipment sizing/rating calculations and drawings (CB, DS, ES, CT, CVT, power transformer, Aux. transformer, NER, suspension/strain Insulators, etc.) | Lot | 1
| 1.2 | Detail design drawings of layout, site plan and sections | Lot | 1
| 1.3 | Substation earthing system design Calculations and drawings (including cross section of grounding conductor and rizer, step voltage, touch voltage, maximum potential rise, main grid resistance, etc. as required) | Lot | 1
| 1.4 | Lightning protection design calculation and drawings (including risk level assessment, protection zone, etc. as required) | Lot | 1
| 1.5 | Short circuit design analysis (including grid short circuit level at the substation and inteconnection lines, etc. as required) | Lot | 1
| 1.6 | Surge/Lightning arrester design calculations and drawings (including protection zone, protection margin, rated volatge, continous voltage, discharge class, etc. as required) | Lot | 1
| 1.7 | Insulation coordination studies | Lot | 1
| 1.8 | Buswork electrical and mechanical calculations and drawings (Including stranded/tubular conductors sizing, continous and short circuit current carring capacity, corona level or surface volatge gradient, electromechanical forces due to wieght, Ice,wind and short circuit for buasbars, gantry and between equipment, post insulator, and etc. as required) | Lot | 1
| 1.9 | Conductors sag and tension calculations and drawings | Lot | 1
| 1.1 | LVAC/LVDC/UPS auxiliary supply systems, EAT and DG sizing, chargers, batteries design calculations and detail drawings | Lot | 1
| 1.11 | Protection, control, fault monitoring/ metering system design calculations, detail drawings and logic diagram together with relays' configuration, setting calculations and studies | Lot | 1
| 1.12 | Substation automation system (SAS) design calculations and detail drawings | Lot | 1
| 1.13 | Telecommunication system design calculations and detail drawings (for communication with NCC/RCC/NSCC) | Lot | 1
| 1.14 | Substation access control system and CCTV design calculations and detail drawings | Lot | 1
| 1.15 | External and internal lighting design calculations and detail drawings | Lot | 1
| 1.16 | LV cables and cable laying design calculations and detail drawings | Lot | 1
| 1.17 | Gantry and steel structures calculations and detail drawings | Lot | 1
| 1.18 | Equipment foundations calculations and detail drawings | Lot | 1
| 1.19 | Main and Aux. Transformers' foundations, plinth, firewall, oil pits, and etc., calculations and detail drawings | Lot | 1
| 1.2 | Cable trenches/ ducts calculations and detail drawings | Lot | 1
| 1.21 | Control building, technical/security staff housings, diesel generator house, storage warehouse, fire water pump house design calculations and detail drawings | Lot | 1
| 1.22 | All relevant substation civil works design calculations and detail drawings to ensure a fully functional substation including borehole, plumbing, landscaping, parking, fence, entrance gate, etc. | Lot | 1
| 1.23 | Substation access road (tarmac) design calculations and detail drawings | Lot | 1
| 1.24 | Substation external access road design calculations and detail drawings (rehabilitation, if any) | Lot | 1
| 1.25 | HVAC air-conditioning design calculations and detail drawings (if any) | Lot | 1
| 1.26 | Drainage, sewage and plumbing works design calculations and detail drawings | Lot | 1
| 1.27 | Water supply system, Water Solar Heating System design calculations and detail drawings (if any) | Lot | 1
| 1.28 | Firefighting system design calculations and detail drawings | Lot | 1
| 1.29 | Other required detail design drawings | Lot | 1
| 1.3 | Design review meeting as specified in the Employer's Requirements Part 2-A Clause 27.3 | Lot | 1
| 1.31 | Submission of complete final as-built drawings of New Kilifi to the Client/Consultant approval | Lot | 1
TOTAL PRICE SCHEDULE 3 NEW KILIFI SUBSTATION Note: Contractor shall include all design services in his proposal, which are necessary to complete the works.

## Schedule_4_SS
SCHEDULE NO. 4
INSTALLATION AND OTHER SERVICES
FOR NEW KILIFI SUBSTATION
Note: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
1 | 2 | 3 | 4 |  |  | 5 |  |  | 6
Item No | Description | Unit | Estimated Quantity | "Foreign Currency (FC1) = USD Foreign Currency (FC2) = EURO Local Currency (KSh) = KENYAN SHILLINGS" |  |  | Total Price
|  |  |  | Installation and other Services |  |  | Installation and other Services
|  |  |  | Unit Price |  |  | (Quantity x Unit Price)
|  |  |  | FC1 | FC2 | Ksh | FC1 | FC2 | Ksh
EQUIPMENT AND MATERIAL
1 | 220kV PRIMARY PLANT
1.1 | 220kV Circuit Breaker (3 phase) 2500A, 40kA - single pole | No. | 6
1.2 | Motorized disconnector (3-phase) 220kV,2500A,40kA, with two (2) earthing switch with earth mat | Set | 4
1.3 | Motorized disconnector (3-phase) 220kV,2500A,40kA, with one (1) earthing switch, and earth mat | Set | 12
1.4 | 220kV, 40kA Motorized earthing switch (3-phase) with earth mat | Set | 2
1.5 | Surge arrester 220kV (1-phase) including surge counter and earth leakage meter | No. | 12
1.6 | Post Insulator | Lot | 1
1.7 | Insulator string (suspension and strain types with hardware fitting) | Lot | 1
1.8 | 220 kV Post type current transformer, for protection and metering, five cores (1-phase) | No. | 18
1.9 | 220 kV Post type current transformer, for metering, two cores (1-phase) | No. | 6
1.10 | 220 kV Capacitive voltage transformer protection and metering three cores (1-phase) | No. | 6
1.11 | 132 kV Capacitive voltage transformer protection and measuring two cores (1-phase) | No. | 18
1.12 | Conductor - Tubular | Lot | 1
1.13 | Conductor - Stranded | Lot | 1
1.14 | Connectors and clamps for tubular conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
1.15 | Connectors and clamps for stranded conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
TOTAL PRICE ITEM 1
2 | 132kV PRIMARY PLANT
2.1 | 132kV Circuit Breaker (3 phase) 1250A, 31.5kA | Set. | 3
2.2 | Motorized disconnector (3-phase), without earth switch, with earth mat | Set | 6
2.3 | Motorized disconnector (3-phase), complete with one integral motorised earth switch, and earth mat | Set | 2
2.4 | 132kV, 31.5kA Motorized earthing switch (3-phase) with earth mat | Set | 2
2.5 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 6
2.6 | Post insulator | Lot | 1
2.7 | Insulator string (suspension and strain types with hardware fitting) | Lot | 1
2.8 | Post type current transformer protection and metering five cores (1-phase) | No. | 3
2.9 | Post type current transformer, for protection, four cores (1-phase) | No. | 6
2.10 | Post type current transformer, for protection,two cores (1-phase) | No. | 6
2.11 | Voltage transformer Protection and metering Two Cores (1-phase) | No. | 6
2.12 | Conductor - Stranded | Lot | 1
2.13 | Connectors and clamps for stranded conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
TOTAL PRICE ITEM 2
3 | POWER TRANSFORMER (P.TR.)
3.1 | Power transformer three phase units HV220/MV132/TV 11kV, 90-110MVA including HV/MV/TV/Neutral Bushing CT's, OLTC, RTCC, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS | No. | 2
3.2 | Fire Detection and Protection System (Nitrogen Injection system) | No. | 2
3.3 | 50 kg wheeled Dry-Powder Fire extinguisher for Power Transformer | No. | 2
TOTAL PRICE ITEM 3
4 | AUXILIARY TRANSFORMER
4.1 | 11/0.415kV, 500kVA, ZNyn11 Earthing & Auxiliary transformers including all accessories as required | No. | 2
4.2 | 11kV, 30A 3-phase cut off fuse | No. | 6
4.3 | 50 kg wheeled Dry-Powder Fire extinguisher for Auxiliary transformer | No. | 2
4.4 | 500A/10s Neutral Earthing Resistor (NER) including all accessories as required | No. | 2
TOTAL PRICE ITEM 4
5 | 220kV & 132 PROTECTION SYSTEMS
5.1 | 220kV Diameter (OHL) Protection System including:
5.1.1 | Main 1 21L Protection(with all required functions as per PSLD) | No. | 2
5.1.2 | Main 2 87L Protection(with all required functions as per PSLD) | No. | 2
5.1.3 | 87T/87NT protection with all required functions as per SLD | No. | 2
5.1.4 | 87HVC protection with all required functions as per SLD | No. | 2
5.1.5 | Auto-Reclose Protection Relay(with all required functions and Voltage Selection Logic as per PSLD) | No. | 2
5.1.6 | All other relays or functions such as over voltage; under voltage; trip relay; trip circuit supervison; pole discordance; synchro check; fuse failure; close relay; lockout relay; short zone, end zone; circuit breaker failure, cubicles, test blocks and test plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the full protection scheme. | Lot | 1
5.1.7 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 12
5.1.8 | Equipment for modification works in remote existing Kabarnet, substation including name tags, differential relays settings and etc.. | Lot | 1
5.2 | Transformer 132kV Side and Neutral Earthin Transformer Protection System including:
5.2.1 | Main 87LVC Protection(with all required functions as per PSLD) | No. | 2
5.2.2 | Backup 67/67(N) Protection(with all required functions as per PSLD) | No. | 2
5.2.3 | Earth Fault 50N/51N (SBEF) Protection (with all required functions as per PSLD) | No. | 2
5.2.4 | 50TV protection with all required functions as per PSLD | No. | 2
5.2.5 | 87NTV protection with all required functions as per PSLD | No. | 2
5.2.6 | All other relays or functions such as over voltage; under voltage; trip relay; trip circuit supervison; pole discordance; synchro check; fuse failure; close relay; lockout relay; short zone, end zone; circuit breaker failure, cubicles, test blocks and test plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the full protection scheme. | Lot | 1
5.2.7 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 5
5.3 | 220kV & 132kV Busbar Protection System
5.3.1 | 220kV Busbar Protection System
5.3.1.1 | 220kV Low Impedance type Busbar Protection Relay ACC. To PSLD drawing and considering future extension | No. | 2
5.3.1.2 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux relays, test and terminal blocks, timers, wiring etc. to make the system complete | No. | 2
5.3.2 | 132kV Busbar Protection System
5.3.2.1 | 132kV Low Impedance type Busbar Protection Relay ACC. To PSLD drawing and considering future extention | No. | 2
5.3.2.2 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux relays, test and terminal blocks, timers, wiring etc. to make the system complete | No. | 2
5.3.2.3 | Low impedance busbar protection system including panels, relays, auxiliary relays, and all accessories for double bus scheme extension/modification scope with compete retesting, recommissioinig and all other modifications | Lot | 1
5.4 | Miscellaneous modification works as necessary to make a complete functional 220 &132kV protection system | Lot | 1
TOTAL PRICE ITEM 5
6 | AVR PROTECTION SYSTEMS
6.2 | Autotransforme Automatic Voltage Regulation System including:
6.2.1 | Automatic Voltage Regulator Relay (AVR) | No. | 2
6.2.2 | Panels with all accessories and auxiliaries, lighting, heating, socket, push buttons, wiring, terminals, test facilities, discrepancy and all other switches, labels, unit measurement indicating lamps, position indicators, alarm announciators, temperature indicators, test block/plug , Labels, etc. and with the following equipment. | No. | 2
TOTAL PRICE ITEM 6
7 | 220132kV SUBSTATION CONTROL SYSTEM
7.1 | Substation automation system including:
7.1.1 | All software and license, Modifications in HMI | Lot | 1
7.1.2 | Bay Control and Protection Units (BCU/BCPU)(with all required functions as per PSLD) | No. | 6
7.1.3 | Bay Control Panels | No. | 2
7.1.4 | Auxiliary and Common Services Bay Control Unit | Lot | 1
7.1.5 | Auxiliary and Common Services Panel including all accessories | Lot | 1
7.1.6 | Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
7.1.7 | Human Machine Interface Systems and Computers | No. | 2
7.1.8 | Any other material for full functionality of the Substation Control System | Lot. | 1
7.1.9 | Fault Monitoring System and Alarm System | Lot | 1
8 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
8.1 | Equipment for Modification works at Remote SS | Lot | 1
9 | TELECOMMUNICATION & NCC/RCC/NSCC
9.1 | Required equipment for Telecommunication and Teleprotection Signalling System | Lot | 1
9.1.1 | Required equipment for Telecommunication SDH System | Lot | 1
9.1.2 | Required equipment for Teleprotection Signalling Equipment Interface Board for Distance & Differential protection relay |  | 1
9.2 | New Firewall system with all necessary Licenses | Lot | 1
9.3 | Required equipment for incorporating substation equipment into the SCADA/EMS System at the NCC/RCC/NSCC | Lot | 1
9.4 | Required equipment for modifications to NCC/RCC/NSCC mimic board (if any) | Lot | 1
9.5 | All necessary licences, hardware, software and configuration needed for the existing network management system (NMS) to create the STM-4 link that forms part of the Optic network from New Kilifi 220/132kV Substation and other Substation to the NCC/RCC/NSCC
9.6 | Required equipment for PABX in RCC including all necessary Licenses, Network switches and any other facilities for communication with NCC,RCC and NSCC | Lot | 1
9.7 | Required equipment and accessories for interconnection between the OPGW and fibre optic cable in communication room | Lot | 1
9.7.1 | Optical Distribution panel for Main Communication room | No | 1
9.7.2 | Optical Distribution Unit (OCDF) 48 cores fiber for Main Communication room | Set | 1
9.7.3 | Digital Distribution Unit (ODF) for 48 cores fiber | Set | 2
9.7.4 | Tail Optical Fiber | Lot | 1
9.7.5 | 48 cores Optical Cable | Lot | 1
9.7.6 | 2M Coaxial Cable | Lot | 1
9.7.7 | PVC Pipe suitable for the distance between entry gantry and communication room | Lot | 1
9.7.8 | Optical Cable plane | Lot | 1
9.7.9 | Steel Tube from junction box to entry of cable channel | Lot | 1
9.7.10 | OPGW Splice Closures joint box with all accessories | Set | 3
9.8 | EPABX system for communication between guard house and individual Staff housings including:
9.8.1 | Exchange | Lot. | 1
9.8.2 | Telephone Equipment | No | 16
9.8.3 | Junction Boxes | Lot | 1
9.8.4 | Cabling | Lot | 1
9.8.5 | Power supply with backup battery | Lot | 1
9.9 | VHF System included a station set and at least 4 portable handsets and batteries and battery chargers, suitable antenna with all accessories (RG, Heliax cabling, AC & DC cabling, indication lamp), supported tower with suitable height | Lot | 1
9.1 | Any other material for full functionality of the Telecommunication System | Lot | 1
TOTAL PRICE ITEM 9
10 | LV CABLES AND ACCESSORIES
10.1 | Auxiliary power and control cabling including single and three phase power cables, control cables required for control; protection; metering and alarms, CTs and CVTs cabe circuits, DC supply cables. | Lot | 1
10.2 | Substation internal fibre optic cabling, coaxilal cables. | Lot | 1
10.3 | Cabling installation including, cable trays, ladders, supports & fixing calmps, accessories, glands, lugs, terminals, rails, labels, cable shoes, fire proof sealing of ducts/conduits/openings etc. | Lot | 1
TOTAL PRICE ITEM 10
11 | EARTHING & LIGHTNING PROTECTION
11.1 | Earthing system (including main earth grid, earth mat, raiser, bonding, connector, clamp, fitting, earth rod and well, inspection earth pits etc. as required) | Lot | 1
11.2 | Lightning protection system (including shield wire, air termination rod, down conductor, equipotential bonding, disconnecting link, etc. as required) | Lot | 1
TOTAL PRICE ITEM 11
12 | SUPPORT STRUCTURES
12.1 | Steel supports for 220kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.2 | Steel supports for 11kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.3 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.4 | Structures for interconnecting 220kV and 132kV switchyards bus (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.5 | Steel supports for 132kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
12.6 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
TOTAL PRICE ITEM 12
13 | "CIVIL WORKS Note: All required material and works shall be included in the quoted price in this section."
13.1 | Site survey | Lot | 1
13.2 | Site clearance including removal of shrubs, bushes, vegetation, buildings, foundations as necessary | Lot | 1
13.3 | Earth works including excavation, backfilling and excavation in rock up to a depth of 2m | Lot | 1
13.4 | Soil Investigation (Geotechnical and geo-electrical) (Boreholes and trial pits) | Lot | 1
13.5 | Temporary works | Lot | 1
13.6 | Grading and landscaping on completion | Lot | 1
13.7 | Surfacing with gravel | Lot | 1
13.8 | Extension and Integration of Drainage system (including: excavation, backfill, channel slopping, lean concrete, reinforcement, formwork, concrete placement, concrete curing, grating plates, filter aggregates and others) | Lot | 1
13.9 | Sewage system (including Polyethylene Pipes, PVC Vent Pipes, Toilet, Septic Tanks with sufficient size, Floor drain, Valves, etc.)
13.9.1 | Underground Septic Tank for control building and Guard house | No. | 1
13.9.2 | Underground Septic Tank for Technical staff Housing and Security staff Housing, | No. | 2
13.9.3 | Polyethylene Pipes, PVC Vent Pipes, Toilet, Floor drain, Valves, etc. | Lot | 1
13.10 | Complete water supply system (potable water and fire water) including borehole, 30,000-liter and 10,000-liter reservoirs (tanks quantity and capacity shall be adequate to serve requirements of control building, staff housings, guard house etc. with automatic level controls), pumps, pipes, valves, control panel, electric motors, indicative gauges/meters, etc.
13.10.1 | Water Pump for Control building, Regional Office and Guard house, as per detail design | No. | 1
13.10.2 | Water Pump for Technical staff Housings and Security staff Housings as per detail design | No. | 1
13.10.3 | Main water supply pressed steel tank (30,000 lit.) with automatic control systmem including foundations | Lot | 1
13.10.4 | Elevated pressed steel water tank (10,000 lit.) with automatic control system including foundations and structureres for control building, guard house, staff housings, etc. | No. | 3
13.10.5 | Water system plumbing and accessories to circulate water from borehole to 30,000-liter reservoir and 10,000-liter elevated water tanks (adjacent to manned buildings) | No. | 1
13.10.6 | Complete solarized borehole including the solar panels, the inverter, controllers, solar pumps and all the accessories | Lot. | 1
13.11 | Salt water filter machine with all accessories connected to the main tank | Lot. | 1
13.12 | Completion and integration of Substation chain link fence shifting, removal and installation works including security for watch and ward during construction phase, as per bid drawings to match the existing | Lot | 1
13.13 | Switchyard chain link fence to match the existing as required | Lot | 1
13.14 | New Substation gates and access control system | Lot | 1
13.15 | Cable trenches / ducts (including: excavation, backfill, channel slopping, lean concrete, reinforcement, formwork, concrete placement, concrete curing, grating plates,supporting angles,Cover Slab and others) | Lot | 1
13.16 | Substation Road and fence Lighting System, With all ralated equipment including Lighting fixture and terminal boxes, Steel lighting poles with related terminals, fuses, fixtures, lamps and etc. , cables and related accessories, distribution boards and etc. | Lot | 1
13.17 | Foundation of 220kV equipment/support structures (including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, galvanized anchor bolt and others) | Lot | 1
13.18 | Foundation of 132kV equipment/support structures (including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, galvanized anchor bolt and others) | Lot | 1
13.19 | Foundation of 11kV equipment/support structures (including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, galvanized anchor bolt and others) | Lot | 1
13.2 | Foundation of gantries and other structures within substation (including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, galvanized anchor bolt and others) | Lot | 1
13.21 | Foundation for Structures for interconnecting 220kV and 132kV switchyards | Lot | 1
13.22 | Miscellaneous foundation to complete the requirements of work | Lot | 1
13.23 | Main Transformer foundation, Plinth and oil drain pits(including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, metal works and fittings and others) | Set | 2
13.24 | Auxiliary and earthing Transformer foundation, Plinth and oil drain pits (including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, metal works and fittings and others) | Set | 2
13.25 | Firewalls for Power Transformers (including: excavation, backfill, reinforced concrete, lean concrete, formatting, grout, reinforcement, metal works and fittings and others) (if any) | Lot | 1
13.26 | Storage Warehouse including building services (e.g. Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), HVAC (fans, heaters, etc.), Fire Detection, hand held and trolley-mounted fire extinguishers and etc.)
13.26.1 | Construction of Storage Warehouse (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, access control, etc. | m2 | 1460
13.26.2 | Wind-driven Cyclone Ventilator for Storage Warehouse, one per slope per span | No. | 20
13.26.3 | Dry-Powder Fire extinguishers, 12 Kg for Storage (as required acc. to bid documents) | No. | 4
13.26.4 | CO2 Fire extinguishers, 6 Kg for Storage (as required acc. to bid documents) | No. | 4
13.26.5 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
13.27 | Diesel generator house Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services (e.g. Lighting, Small Power System, Fire Detection and hand-held fire extinguishers)
13.27.1 | Construction of Diesel generator house (including Excavation, concrete works, backfilling, and etc.) and Building services (e.g. Lighting, Small Power System, Fire Detection and hand-held fire extinguishers) Note: As per contractor's detail design and proposed package, the building size shall be considered accordingly without any surcharge | m2 | 40
13.27.2 | Dry-Powder Fire extinguishers, 12 Kg for Storage (as required acc. to bid documents) | No. | 1
13.28 | Fire water pump house Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services (e.g. Lighting, Small Power System, HVAC (fans, etc.), Fire Detection hand held and trolley-mounted fire extinguishers and etc.) and borehole with underground reservoir (with adequate capacity to Client/Consultant Approval) of adequate capacity with automatic level control to serve requirements of substation yard and buildings, yard hydrant system, NFPA-listed and jockey pumps, and other required equipment/works to make a complete and functional system
13.28.1 | Construction of Fire water pump house (including Excavation, concrete works, backfilling, and etc.) and Building services (e.g. Lighting, Small Power System, HVAC (fans, etc.), Fire Detection hand held and trolley-mounted fire extinguishers and etc.) Note: As per contractor's detail design and proposed package, the building size shall be considered accordingly without any surcharge. | m2 | 40
13.28.2 | 50,000 litres fire water supply tank with automatic level control | Lot | 1
13.28.3 | Hydrant system for yard | Set | 1
13.28.4 | Fire pump package (NFPA-listed and jockey pumps, etc.) | Set | 1
13.28.5 | Other required equipment/works to make a complete and functional firefighting system | Lot | 1
13.29 | Construction of substation control building including control, protection and telecommunication systems Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, HVAC, Water Solar Heating, Fire Detection and fire extinguishers (handheld and trolley-mounted), fire blankets, access control, etc.
13.29.1 | Construction of new substation control building (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, access control, etc. | m2 | 440
13.29.2 | Complete Split Unit, 9000 BTU/hr for Communication Room, Meeting Room, Office, Operator & Scada Room | No | 8
13.29.3 | Complete Split Unit, 12000 BTU/hr for AC/DC Room | No. | 4
13.29.4 | Complete Split Unit-24000 BTU/hr for Relay Room | No. | 4
13.29.5 | Exhaust Fan, 270 m3/hr for Toilets | No. | 2
13.29.6 | Hood-450 CFM for Kitchen | No. | 1
13.29.7 | Exhaust Fan, 2900 m3/hr for Battery Room (suitable for hazardous area) | No. | 4
13.29.8 | Dry-Powder Fire extinguishers, 12 Kg for Store, AC/DC room, Archive Room, Communication Room, Meeting Room, Office, Operator & Scada Room, Relay Room, and Corridor (as required acc. to bid documents) | No. | 18
13.29.9 | CO2 Fire extinguishers, 6 Kg for Store, AC/DC room, Archive Room, Communication Room, Meeting Room, Office, Operator & Scada Room, Relay Room, and Corridor (as required acc. to bid documents) | No. | 18
13.29.10 | Solar Water Heater with backup electric heating element | Lot | 1
13.29.11 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower with Faucet, Basin Faucet, Basin, Sink, Eye Wash, Pipes, Valves, etc.) | Lot | 1
13.3 | Battery room shall include automatic full redundant double fans and ventilating louver against the fan, eyewash and wide-windows shall be avoided to prevent batteries exposure to sun shine (Modification and Blocking or removal of windows, improvement of ventilation in the existing battery room) | Lot | 1
13.31 | Fire Detection and Alarm System (for Transformers and Buildings) | Lot | 1
13.32 | Substation internal access road to bituminous standards complete with drainage facilities and culverts as necessary suitable for heavy machine's traffic, as per bid drawings (including road leveling, lean conceret, prefabricated concrete kerb, base and sub-base, and surfacing as per detail design) | Lot | 1
13.33 | Upgrading approximately 1.5km of the existing murram external access road to bituminous standard and subject to Client's approval Note: The access road length shall be included in the quoted price as required, and no surcharge is accepted. | km | 1.5
13.34 | Construction of five meter wide and approximately 350m long murram road for fire break around the inner side of the substation fencing and as per the layout drawing. | m | 350
13.35 | Construction of approximately 220m Bituminous standard road from substation to technical staff and security housing, including the internal access roads | m | 220
13.36 | Retaining wall should be constructed when there is a considerable level difference in the site. | Lot | 1
13.37 | All required additional works to make the system complete and functional | Lot | 1
TOTAL PRICE ITEM 13
14 | AUXILIARY SUPPLY
14.1 | LVAC system
14.1.1 | AC Main and distribution panels, AC distribution outdoor cubicles, with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | Lot | 1
14.1.2 | Oil treatment panel with fuse box socket and accessories (including heavy duty outlet socket, fuses, glands, etc.) | No. | 1
14.1.3 | Diesel Generator 250kVA including generator control and protection panel and all peripheral equipment, reservior(s), (foundations, structure), and accessories. | No. | 1
14.1.4 | Any other material for full functionality of the LVAC System | Lot. | 1
14.2 | LVDC system
14.2.1 | Supply, Installation, wiring, integration, test and commissioning of 110Vdc Main and distribution panels, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) as per 110Vdc SLD and Employer's Requirement | Lot | 1
14.2.2 | Supply, Installation, wiring,integration, test and commissioning of 48Vdc distribution panel, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) as per 48Vdc SLD and Epmployer's Requirement | Lot | 1
14.2.3 | Any other material for full functionality of the LVDC System | Lot. | 1
14.2.4 | 415V ac Uninterruptible Power Supply including isolating by-pass transformers, inverters, static switch, manual bypass switch, panels & distribution boards | Set | 2
14.2.5 | 400Ah battery bank (Ni-Cd) Batteries | Nos. | 2
14.2.6 | 100A Float cum boost charger | Nos. | 2
TOTAL PRICE ITEM 14
15 | TARIFF METERING
15.1 | Tariff metering System for 220kV OHL, complete with wiring, accessories and etc. including:
15.1.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
15.1.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
15.2 | Tariff metering System for Power Transformer, complete with wiring, accessories etc. and including:
15.2.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
15.2.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2S class accuracy | No. | 2
15.3 | Metering data collection and communication system, complete with fibre optic cabling, accessories, Each kind of energy meters software and communication ports. All media and accessories in order to transferring Energy meter measuring values to remote center according to both KETRACO and KPLC required specification. | Lot | 1
15.4 | Metering panel with all accessories and auxiliaries, lighting, heating, socket, wiring, terminals, test facilities, and all other switches, labels, test block/plug , Labels, etc. | No. | 2
15.5 | All other related relays, racks, Voltage/Current test block, cubicles, terminals, As needed to complete the metering system. | Lot | 1
TOTAL PRICE ITEM 15
16 | MISCELLANEOUS
16.1 | Required Bay Marshalling Kiosk | Lot | 1
16.2 | Completion of CCTV System, with all related equipment for indoor and outdoor including Cameras of required type and specifications with Poles, Recorder and storage and monitor, Switch, Cabling, Boxes, Fixings and brackets and etc. | Lot | 1
16.3 | Padlocks / Keys (for panels, outdoor equipments, doors, etc.) | Lot | 1
16.4 | Equipment/Bay labels, safety warning plates, road signages, room name plates, etc. | Lot | 1
16.5 | Overhead crane double girder type for storage warehouse | Lot | 1
16.6 | 50 Mbps symmetric internet bandwidth in the control room building for scalable and future-proof connectivity to support basic IT Functions (Email, ERP access, VoIP, Patch Management) and Video Surveillance Streaming and Remote Support Capabilities . Design should allow easy upgrades of bandwidth and hardware as needs evolve. | Lot | 1
16.7 | Any other items not included above but required to complete the project successfully. (Tenderer shall specify and include breakdown of price in his proposal) | Lot | 1
TOTAL PRICE ITEM 16
17 | MOBILIZATION, SITE TRANSPORT, SITE OFFICE AND PERMANENT LIVING ACCOMMODATION Provision as per Employer's Requirements, Clause 27 & 28 of Part 2-A of Employer's Requirements
17.1 | Vehicles as per part 2-A, Clause 28
17.1.1 | Operation, maintenance, regular upkeep of the vehicles including spares, consumables and services of driver/mechanic experienced in desert driving, insurance etc. for the entire duration of the contract as per part 2-A, Clause 28 | months | 36
17.2 | Temporary Works, Site Office, Site Storage and Living Accomodation as per Clause 27, 28 and 29 of Part 2-A | Lot | 1
17.2.1 | Mobilization including all required equipment, machineries, devices, tools and facilities as specified in Clause 2.6 of section III of Part1 and Clause 27 and 28 of Part 2-A | Lot | 1
17.2.2 | Site Office fully equipped/furnished as specified in the Employer's Requirements and with fully furnished kitchenettes, Storage Facilities as per Clause 27 of Part 2-A | months | 24
17.2.3 | Site power supply from local power network, etc. | Lot | 1
17.2.4 | Site temporary fencing with barbed wire | Lot | 1
17.2.5 | Project sign boards | Lot | 1
17.2.6 | Roads, sidewalks and parking | Lot | 1
17.2.7 | Road, fence and area lighting system with all ralated equipment including Lighting fixture and terminal boxes, Steel lighting poles with related terminals, cables, fuses, fixtures, lamps, related accessories and AC distribution outdoor cubicles | Lot | 1
17.2.8 | Storage facilities | Lot | 1
17.2.9 | First aid facilities | Lot | 1
17.2.10 | Ambulance facilities | Lot | 1
17.2.11 | Drainage System | Lot | 1
17.2.12 | Sewage system | Lot | 1
17.2.13 | Water Supply System | Lot | 1
17.2.14 | Site Toilets | Lot | 1
17.2.15 | Watch and ward and access control to site during construction | Lot | 1
17.3 | Staff Housings for Permanent Living of Technical and Security Personnel as per Clause 27 of Part 2-A
17.3.1 | Technical staff Housing Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services e.g. Lighting, Small Power System, Water Supply and Sewage System, HVAC (DX split units, fans, etc.), Water Solar Heating, Fire Detection and hand held fire extinguishers,fire blankets, fully furnished | Units | 4
17.3.1.1 | Construction of Technical staff Housing (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System, Water Supply and Sewage System, access control, etc. | m2 | 420
17.3.1.2 | Complete Split Unit, 9000 BTU/hr for Bedrooms | No. | 8
17.3.1.3 | Complete Split Unit, 12000 BTU/hr for Living and Dining Rooms | No. | 8
17.3.1.4 | Exhaust Fan, 270 m3/hr for Toilets | No. | 4
17.3.1.5 | Hood-450 CFM for Kitchen | No. | 4
17.3.1.6 | Dry-Powder Fire extinguishers, 12 Kg for Bedrooms, Living and Dining Room | No. | 12
17.3.1.7 | CO2 Fire extinguishers, 6 Kg for Bedrooms, Living and Dining Room | No. | 12
17.3.1.8 | Solar Water Heater with backup electric heating element | Lot | 1
17.3.1.9 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
17.3.1.10 | Other furniture and devices and facilities as in Clause 27.2 (TV, wi-fi, IP phone, refrigrator, freezer, oven, hood, cookers, washing machines etc.) | Lot | 1
17.3.2 | Security staff Housing Civil work (including Excavation, concrete works, backfilling, and etc.) together with building services e.g. Lighting, Small Power System, Water Supply and Sewage System, HVAC (DX split units, fans, etc.), Water Solar Heating, Fire Detection and hand held fire extinguishers,fire blankets, fully furnished | Units | 4
17.3.2.1 | Construction of Security staff Housing (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System, Water Supply and Sewage System, access control, etc. | m2 | 112
17.3.2.2 | Complete Split Unit,18000 BTU/hr for Staff Rooms | No. | 4
17.3.2.3 | Exhaust Fan, 270 m3/hr for Toilets | No. | 4
17.3.2.4 | Hood-450 CFM for Kitchen | No. | 4
17.3.2.5 | Dry-Powder Fire extinguishers, 12 Kg for Staff Rooms | No. | 4
17.3.2.6 | CO2 Fire extinguishers, 6 Kg for Staff Rooms | No. | 4
17.3.2.7 | Solar Water Heater with backup electric heating element | Lot | 1
17.3.2.8 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
17.3.2.9 | Other furniture and devices and facilities as in Clause 31.2 (refrigrator, freezer, oven, washing machines, hood, IP phone, etc.) | Lot | 1
17.3.3 | Security fence for the staff housings as per the standard stated on 2A-Employer's requirement | m | 310
17.4 | Site Internet connection and facilities | Lot | 1
17.5 | TV and Cable TV network | Lot | 1
17.6 | 50 Mbps symmetric internet bandwidth for technical staffs and security housing for scalable and future-proof connectivity to support basic IT Functions (Email, ERP access, VoIP, Patch Management) and Video Surveillance Streaming and Remote Support Capabilities . Design should allow easy upgrades of bandwidth and hardware as needs evolve. | Lot | 1
TOTAL PRICE ITEM 17
18 | FACTORY ACCEPTANCE TESTS
Provision as per Employers Requirements: - Part 2-A, Clause 18.1; and - Part 2-B, Relevant Clauses for Testing and Inspection
18.1 | Power transformers FAT | Lot | 1
18.2 | Auxiliary transformers FAT | Lot | 1
18.3 | Instrument transformers FAT | Lot | 1
18.4 | Circuit breakers FAT | Lot | 1
18.5 | Disconnectors & earth switches FAT | Lot | 1
18.6 | Surge arrestors FAT | Lot | 1
18.7 | Conductors, shield wires, OPGW, clamps and connectors FAT | Lot | 1
18.8 | Protection, Control & Metering Panels FAT | Lot | 1
18.9 | Substation Automation and Control System FAT | Lot | 1
18.10 | Telecommunication Equipment FAT | Lot | 1
18.11 | 110Vdc, 48Vdc Batteries, Battery Chargers and UPS FAT | Lot | 1
18.12 | AC and DC Distribution Panels FAT | Lot | 1
18.13 | Diesel Generator | Lot | 1
18.14 | Gantries, Steel Structures and Accessories FAT | Lot | 1
TOTAL PRICE ITEM 18
19 | TRAINING
19.1 | Provision as per Part 2-A, Clause 28.3 of Employers Requirements
19.1.1 | Communication & Substation Control System– Application & Design (3 Design Engineers and 3 O&M Engineers for 3 weeks) | Lot | 1
19.1.2 | Civil/ Structural Design Training (for 3 weeks for 4 Design Engineers and 2 TSP Engineers) | Lot | 1
19.2 | On shore Training | Lot
19.2.1 | Site Operation and Maintenance Training for atleast 10 Engineers for 2 weeks | Lot | 1
TOTAL PRICE ITEM 19
20 | INTERNSHIP & GRADUATE EMPLOYMENT
Provision as per Part 2-A, Clause 27.4 of Employers Requirements
20.1 | Graduates Employment (2 Engineers) | months | 24
20.2 | Graduate Internship (2 Engineers) | months | 24
TOTAL PRICE ITEM 20
21 | Climate Change Impact Mitigation
21.1 | Climate Change Impact Mitigation as per Clause 30 Part 2-A- Scope & General Requirements: The contractor shall plant trees worth KES 5,000,000 or at least 30,000 trees whichever is higher | Lot | 1
21.2 | CSR as per Clause 31 Part 2-A- Scope & General Requirements | Lot | 1 |  |  | 10000000
TOTAL PRICE ITEM 21
22 | PRE-COMMISSIONING, COMMISSIONING AND END-TO-END TESTING
22.1 | Substation Pre-commissioning, commissioning and end-to-end testing including NCC/RCC/NSCC signaling and remote end relay settings modifications. | Lot | 1
TOTAL PRICE ITEM 22
TOTAL PRICE SCHEDULE 4 NEW KILIFI SUBSTATION Note: Contractor shall include and consider all activities which are necessary to complete the project works (including construction, erection, installation, mobilization, site transportation and accomodation, modification, replacement, relocation, tests, pre-commissioning, commissioning, training, internship and etc. as required)

## Schedule_5_Grand Summary
SCHEDULE NO. 5
GRAND SUMMARY OF PRICES FOR NEW KILIFI SUBSTATION
1 | 2 | 3 | 4 | 5
Item No | Description | Total Price
|  | FC1 | FC2 | KSh
1 | Total of Schedule No. 1 NEW KILIFI SS Plant, Equipment and Mandatory Spare Parts Supplied from Abroad
2 | Total of Schedule No. 2 NEW KILIFI SS Plant, Equipment and Mandatory Spare Parts Supplied from within Employer's Country
3 | Total of Schedule No. 3 NEW KILIFI SS Design Services
4 | Total of Schedule No. 4 NEW KILIFI SS Installation and other Services
TOTAL PRICES NEW KILIFI SUBSTATION (SCHEDULES 1-4)
TOTAL PRICES NEW KILIFI SUBSTATION
TOTAL PRICE NEW KILIFI SUBSTATION IN KENYAN SHILLINGS

## Schedule_6_Recommended Spares
SCHEDULE NO. 6
RECOMMENDED SPARE PARTS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Item No | Description | Country of Origin | Unit | Estimated Quantity | Foreign Manufacture Price (CIP) | Local Manufacture Price (CIP) | Total Price for Estimated Quantity
[5 empty] | FC | KSh | FC | KSh
SCHEDULE NO. 6
RECOMMENDED SPARE PARTS
1 | 2 | 3 | 5 | 4 | 6 | 7 | 8 | 9
Item No | Description | Country of Origin | Unit | Estimated Quantity | Foreign Manufacture Price (CIP) | Local Manufacture Price (CIP) | Total Price for Estimated Quantity
[5 empty] | FC (usd) | KSh | FC (usd) | KSh
1 | 220kV Circuit breaker (3-phase) |  | No. | 1
2 | 132kV Circuit breaker (3-phase) |  | No. | 1
3 | 220 kV Disconnector motorised (3 phase) complete with two integrated motorised earth switch |  | No. | 1
4 | 220 kV Disconnector motorised (3 phase) complete with one integrated motorised earth switch |  | No. | 2
5 | 132kV Disconnector, motorised (3-phase) complete without integral motorised earth switch |  | No. | 1
6 | 132kV Disconnector, motorised (3-phase) complete with one integral motorised earth switch |  | No. | 1
7 | 33kV Disconnector, motorised (3-phase) complete without earth switch |  | No. | 0
8 | 220kV Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 1
9 | 132kV Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 1
10 | 33kV Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 0
11 | 132kV Post type current transformer Protection and Measuring five Cores (1-phase) |  |  | 1
12 | 132kV Post type current transformer Protection and Measuring Six Cores (1-phase) |  | No. | 1
13 | 132kV Post type current transformer Protection and Measuring Five Cores (1-phase) |  | No. | 1
14 | 220kV Post type current transformer High Accuracy Tariff Metering Three Cores (1-phase) |  | No. | 1
15 | 132kV Post type current transformer High Accuracy Tariff Metering Two Cores (1-phase) |  | No. | 0
16 | 220kV Capacitive voltage transformer Protection and Measuring Three Cores (1-phase) |  | No. | 1
17 | 132kV Capacitive voltage transformer Protection and Measuring Two Cores (1-phase) |  | No. | 1
18 | 220kV Post Insulator |  | % | 10
19 | 132kV Post insulator |  | % | 10
20 | 220kV Strain insulator |  | % | 10
21 | 132kV Strain insulator |  | % | 10
22 | 132kV Conductor - Tubular |  | % | 10
23 | 132kV Conductor - Stranded |  | % | 10
24 | 132kV Connectors - Tube |  | % | 10
25 | 132kV Connectors - Stranded |  | % | 10
26 | 33kV Conductor - Stranded |  | % | 10
27 | 33kV Connectors - Stranded |  | % | 10
28 | Line distance protection relay |  | No. | 1
29 | Line differential protection relay type 1 |  | No. | 1
30 | Line differential protection relay type 2 |  | No. | 1
31 | Bay Control and protection relay |  | No. | 1
32 | Transformer differential protection relay |  | No. | 1
33 | Station LAN Switches |  | No. | 1
34 | TARIFF METER |  | No. | 2
35 | 50/51(N) Protection relay |  | No. | 1
TOTAL PRICE ITEMS

## Price Schedule Summary
SUMMARY OF PRICE SCHEDULE FOR New Kilifi SUBSTATION OF BID PACKAGE #5
1 | 2 | 3 | 4
Item No | Description | Total Price (1USD= ……... KSh)
|  | From Abroad (USD) | From Local (KSh)
1 | Total of Schedule No. 1A NEW KILIFI SS Plant, Equipment and Mandatory Spare Parts Supplied from Abroad
Main Equipment
1.1 | 220kV PRIMARY PLANT
1.2 | 132kV PRIMARY PLANT
1.3 | POWER TRANSFORMER (P.TR.)
1.4 | AUXILIARY TRANSFORMER
1.5 | 220kV PROTECTION SYSTEMS
1.6 | 132KV PROTECTION SYSTEMS
1.7 | 220/132kV SUBSTATION CONTROL SYSTEM
1.8 | TELECOMMUNICATION & NCC/RCC/NSCC
1.9 | LV CABLES AND ACCESSORIES
1.10 | EARTHING & LIGHTNING PROTECTION SYSTEMS
1.11 | SUPPORT STRUCTURES AND GANTRIES
1.12 | AUXILIARY SUPPLY
1.13 | TARIFF METERING
1.14 | MISCELLANEOUS
1.15 | Site Transport as per Employer's Requirements, Clause 32
1.16 | Total of Main Equipment
Spare Parts
1.17 | 220kV PRIMARY PLANT
1.18 | 132kV PRIMARY PLANT
1.19 | POWER TRANSFORMER (P.TR.)
1.20 | AUXILIARY TRANSFORMER
1.21 | 220kV PROTECTION SYSTEMS
1.22 | 132KV PROTECTION SYSTEMS
1.23 | 220/132kV SUBSTATION CONTROL SYSTEM
1.24 | LV CABLES AND ACCESSORIES
1.25 | AUXILIARY SUPPLY
1.26 | TARIFF METERING
1.27 | MISCELLANEOUS
1.28 | Total of Spare Parts
2 | Total of Schedule No. 2A NEW KILIFI SS Plant, Equipment and Mandatory Spare Parts Supplied from Within the Employer's Country
Main Equipment
2.1 | 220kV PRIMARY PLANT
2.2 | 132kV PRIMARY PLANT
2.3 | POWER TRANSFORMER (P.TR.)
2.4 | AUXILIARY TRANSFORMER
2.5 | 220kV PROTECTION SYSTEMS
2.6 | 132KV PROTECTION SYSTEMS
2.7 | 132/33kV SUBSTATION CONTROL SYSTEM
2.8 | TELECOMMUNICATION & NCC/RCC/NSCC
2.9 | LV CABLES AND ACCESSORIES
2.10 | EARTHING & LIGHTNING PROTECTION SYSTEMS
2.11 | SUPPORT STRUCTURES AND GANTRIES
2.12 | AUXILIARY SUPPLY
2.13 | TARIFF METERING
2.14 | MISCELLANEOUS
2.15 | Site Transport as per Employer's Requirements, Clause 32
2.16 | Total of Main Equipment
Spare Parts
2.17 | 132kV PRIMARY PLANT
2.18 | 33kV PRIMARY PLANT
2.19 | POWER TRANSFORMER (P.TR.)
2.2 | AUXILIARY TRANSFORMER
2.21 | 132kV PROTECTION SYSTEMS
2.22 | 33KV PROTECTION SYSTEMS
2.23 | 220/132 kV SUBSTATION CONTROL SYSTEM
2.24 | LV CABLES AND ACCESSORIES
2.25 | AUXILIARY SUPPLY
2.26 | TARIFF METERING
2.27 | MISCELLANEOUS
2.28 | Total of Spare Parts
3 | Total of Schedule No. 3A NEW KILIFI SS Design Services
4 | Total of Schedule No. 4A NEW KILIFI SS Civil Works, Installation and other Services
4.1 | 220kV PRIMARY PLANT
4.2 | 132kV PRIMARY PLANT
4.3 | POWER TRANSFORMER (P.TR.)
4.4 | AUXILIARY TRANSFORMER
4.5 | 220kV PROTECTION SYSTEMS
4.6 | 132KV PROTECTION SYSTEMS
4.7 | 220/132kV SUBSTATION CONTROL SYSTEM
4.8 | TELECOMMUNICATION & NCC/RCC/NSCC
4.9 | LV CABLES AND ACCESSORIES
4.10 | EARTHING & LIGHTNING PROTECTION SYSTEMS
4.11 | SUPPORT STRUCTURES
4.12 | CIVIL WORKS
4.13 | AUXILIARY SUPPLY
4.14 | TARIFF METERING
4.15 | MISCELLANEOUS
4.16 | Mobilization, Site Transport, Site Office Provision as per Employer's Requirements, Clause 27, 28 & 29 of Part 2-A of Employer's Requirements
4.17 | INTERNSHIP and EMPLOYMENT
TOTAL PRICES NEW KILIFI SUBSTATION (SCHEDULES 1A-4A)
TOTAL PRICE NEW KILIFI SUBSTATION IN KENYAN SHILLINGS