## Schedule 1A_SS
SCHEDULE NO. 1A
PLANT, EQUIPMENT AND MANDATORY SPARE PARTS SUPPLIED FROM ABROAD
FOR KIMUKA SUBSTATION
Note 1: All proposed mandatory spare parts for each equipment or system shall be specified in detail by Bidders.
Note 2: All main and spare equipment shall be provided for proper operation in four altitude categories (to optimize main equipment/ spare parts and achieve interchangeability at country level), including 1000, 1500, 2000 and 2500 meter above sea level. In case of other range may has been mentioned in the schedules of technical information (Part 2-E), the higher altitude category shall be considered.
Note 3: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
| Item No | Description | Country of Origin | Unit | Estimated Quantity | Foreign Currency (FC1) = (FC2) = |  | Total Price
[6 empty] | Foreign Manufacture |  | Foreign Manufacture
[6 empty] | Unit Price (CIP) |  | (Quantity x Unit Price)
[6 empty] | FC1 | FC2 | FC1 | FC2
| 1 | 400kV PRIMARY PLANT
Main Equipment
| 1.1 | Circuit Breaker single pole operated, 3 phase |  | No. | 10
Relevant Mandatory Spare Parts
| 1.1.1 | Trip coil |  | No. | 3
| 1.1.2 | Close coil |  | No. | 2
| 1.1.3 | Anti pumping relay |  | No. | 1
| 1.1.4 | Density blocking relay |  | No. | 1
| 1.1.5 | Density meter |  | No. | 1
| 1.1.6 | Heater |  | No. | 2
| 1.1.7 | Motor for operating mechanism |  | No. | 1
| 1.1.8 | Complete pole including fixed and moving contacts, pull rod, etc. |  | No. | 3
Relevant Peripheral Devices/Material
| 1.1.9 | Gas filling devices |  | No. | 1
| 1.1.10 | SF6 gas |  | % | 20% of required volume for first filling of CBs
| 1.1.11 | SF6 gas leakage detector |  | No. | 1
Main Equipment
| 1.2 | Motorized Disconnector (3-phase), complete with one integral motorised earth switch, and earth mat |  | No. | 20
Relevant Mandatory Spare Parts
| 1.2.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-ES (3-phase) |  | No. | 2
| 1.2.2 | Motorized operating mechanism suitable for DS-ES |  | No. | 2
Main Equipment
| 1.3 | Motorized Disconnector (3-phase), complete with two integral motorised earth switches and earth mat |  | No. | 6
Relevant Mandatory Spare Parts
| 1.3.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-2ES (3-phase) |  | No. | 1
| 1.3.2 | Motorized operating mechanism suitable for DS-2ES |  | No. | 1
Main Equipment
| 1.4 | Motorized Earthing switch (3-phase), with earth mat |  | No. | 2
| 1.5 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 18
Relevant Mandatory Spare
| 1.5.1 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 2
Main Equipment
| 1.6 | Post insulator |  | Lot | 1
Relevant Mandatory Spare
| 1.6.1 | Post insulator of all types |  | % | 10%
Main Equipment
| 1.7 | Insulator string (Suspension and Strain types with harware fitting) |  | Lot | 1
Relevant Mandatory Spare
| 1.7.1 | Insulator string of all types (Suspension and Strain types with harware fitting) |  | % | 10%
Main Equipment
| 1.8 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) |  | No. | 30
Relevant Mandatory Spare
| 1.8.1 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) |  | No. | 3
Main Equipment
| 1.9 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) |  | No. | 12
Relevant Mandatory Spare
| 1.9.1 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) |  | No. | 1
Main Equipment
| 1.10 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) |  | No. | 12
Relevant Mandatory Spare
| 1.10.1 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) |  | No. | 1
Main Equipment
| 1.11 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) |  | No. | 12
Relevant Mandatory Spare
| 1.11.1 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) |  | No. | 1
Main Equipment
| 1.12 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) |  | No. | 12
Relevant Mandatory Spare
| 1.12.1 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) |  | No. | 1
Main Equipment
| 1.13 | Tubular Conductor |  | Lot | 1
Relevant Mandatory Spare
| 1.13.1 | Tubular Conductor of all types |  | % | 10%
Main Equipment
| 1.14 | Stranded Conductor |  | Lot | 1
Relevant Mandatory Spare
| 1.14.1 | Stranded Conductor of all types |  | % | 10%
Main Equipment
| 1.15 | Connectors and Clamps for Tubular Conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
Relevant Mandatory Spare
| 1.15.1 | Connectors and Clamps for Tubular Conductors of all types (together with stainless steel nuts, bolts, bimetal) |  | % | 10%
Main Equipment
| 1.16 | Connectors and Clamps for Stranded Conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
Relevant Mandatory Spare
| 1.16.1 | Connectors and Clamps for Stranded Conductors of all types (together with stainless steel nuts, bolts, bimetal) |  | % | 10%
Main Equipment
| 1.17 | Online monitoring system for 400kV Circuit Breaker |  | No. | 10
Remote End Substation_ISINYA
| 1.18 | All required material such as conductors, fittings , connectord and calmps and etc as required regarding to connection of the 400kV Suswa-1 to switchyard 400kV with completion the connection between of the feeder's equipment as per scope of work |  | No. | 10
1.19
TOTAL PRICE ITEM 1
TOTAL PRICE ITEM 1_Spare Parts
| 2 | 220kV PRIMARY PLANT
Main Equipment
| 2.1 | Circuit breaker single pole operated, 3 phase |  | No. | 6
Relevant Mandatory Spare Parts
| 2.1.1 | Trip coil |  | No. | 3
| 2.1.2 | Close coil |  | No. | 1
| 2.1.3 | Anti pumping relay |  | No. | 1
| 2.1.4 | Density blocking relay |  | No. | 1
| 2.1.5 | Density meter |  | No. | 1
| 2.1.6 | Heater |  | No. | 2
| 2.1.7 | Motor for operating mechanism |  | No. | 1
| 2.1.8 | Complete pole including fixed and moving contacts, pull rod, etc. |  | No. | 2
Relevant Peripheral Devices/ Material
| 2.1.9 | Gas filling devices |  | No. | 1
| 2.1.10 | SF6 gas |  | % | 20% of required volume for first filling of CBs
| 2.1.11 | SF6 gas leakage detector |  | No. | 1
Main Equipment
| 2.2 | Motorized Disconnector (3-phase), complete with one integral motorised earth switch, and earth mat |  | No. | 12
Relevant Mandatory Spare Parts
| 2.2.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-ES (3-phase) |  | No. | 1
| 2.2.2 | Motorized operating mechanism suitable for DS-ES |  | No. | 1
Main Equipment
| 2.3 | Motorized Disconnector (3-phase), complete with two integral motorised earth switches and earth mat |  | No. | 4
Relevant Mandatory Spare Parts
| 2.3.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-2ES (3-phase) |  | No. | 1
| 2.3.2 | Motorized operating mechanism suitable for DS-2ES |  | No. | 1
Main Equipment
| 2.4 | Motorized Earthing switch (3-phase), with earth mat |  | No. | 2
| 2.5 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 12
Relevant Mandatory Spare Parts
| 2.5.1 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 1
Main Equipment
| 2.6 | Post insulator |  | Lot | 1
Relevant Mandatory Spare Parts
| 2.6.1 | Post insulator of all types |  | % | 10%
Main Equipment
| 2.7 | Insulator string (Suspension and Strain types with harware fitting) |  | Lot | 1
Relevant Mandatory Spare Parts
` | 2.7.1 | Insulator string of all types (Suspension and Strain types with harware fitting) |  | % | 10%
Main Equipment
| 2.8 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) |  | No. | 18
Relevant Mandatory Spare Parts
| 2.8.1 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) |  | No. | 2
Main Equipment
| 2.9 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) |  | No. | 6
Relevant Mandatory Spare Parts
| 2.9.1 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) |  | No. | 1
Main Equipment
| 2.10 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) |  | No. | 6
Relevant Mandatory Spare Parts
| 2.10.1 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) |  | No. | 1
Main Equipment
| 2.11 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) |  | No. | 12
Relevant Mandatory Spare Parts
| 2.11.1 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) |  | No. | 1
Main Equipment
| 2.12 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) |  | No. | 6
Relevant Mandatory Spare Parts
| 2.12.1 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) |  | No. | 1
Main Equipment
| 2.13 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) |  | No. | 6
Relevant Mandatory Spare Parts
| 2.13.1 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) |  | No. | 1
Main Equipment
| 2.14 | Tubular Conductor |  | Lot | 1
Relevant Mandatory Spare Parts
| 2.14.1 | Tubular Conductor of all types |  | % | 10%
Main Equipment
| 2.15 | Stranded Conductor |  | Lot | 1
Relevant Mandatory Spare Parts
| 2.15.1 | Stranded Conductor of all types |  | % | 10%
Main Equipment
| 2.16 | Connectors and Clamps for Tubular Conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
Relevant Mandatory Spare
| 2.16.1 | Connectors and Clamps for Tubular Conductors of all types (together with stainless steel nuts, bolts, bimetal) |  | % | 10%
Main Equipment
| 2.17 | Connectors and Clamps for Stranded Conductors (together with stainless steel nuts, bolts, bimetal) |  | Lot | 1
Relevant Mandatory Spare
| 2.17.1 | Connectors and Clamps for Stranded Conductors of all types (together with stainless steel nuts, bolts, bimetal) |  | % | 10%
| 2.18 | Remote End Substation_ISINYA
| 2.18.1 | 220 kV Surge arrester (1-phase) including surge counter and earth leakage meter |  | No | 3
| 2.18.2 | PI |  | No | 3
TOTAL PRICE ITEM 2
TOTAL PRICE ITEM 2_Spare Parts
| 3 | AUTO TRANSFORMER (A.TR.)
Main Equipment
| 3.1 | Auto transformer (3-phase units) with tertiary winding HV400/LV220/TV11kV, 200MVA including HV/LV/TV/NV Bushing CT's, OLTC, RTCC,OLCM, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS |  | No. | 2
Mandatory Spare Parts
| 3.1.1 | Bushing for HV side |  | No. | 1
| 3.1.2 | Bushing for LV side |  | No. | 1
| 3.1.3 | Bushing for Neutral H.V. side |  | No. | 1
| 3.1.4 | Bushing and Insulator for T.V. side |  | Set | 1
| 3.1.5 | Oil Directed Pressure Relief Device (main tank) |  | No. | 1
| 3.1.6 | Oil Directed Pressure Relief Device (OLTC) |  | No. | 1
| 3.1.7 | Buchholz Relay |  | No. | 1
| 3.1.8 | Oil Level Indicator for Main Tank |  | No. | 1
| 3.1.9 | Oil Level Indicator for OLTC |  | No. | 1
| 3.1.10 | Oil Surge Relay for OLTC |  | No. | 1
| 3.1.11 | Cooling Fans |  | No. | 2
| 3.1.12 | Winding Temperature Indicator |  | No. | 1
| 3.1.13 | Oil Temperature Indicator |  | No. | 1
| 3.1.14 | Valves for Radiators |  | Set | 1
| 3.1.15 | Contactors and required accessories eg. Aux. Relay, MCB, Control relay, and etc. (in Marshalling Kiosk) |  | No. | 1 for Each Type
| 3.1.16 | Transducer |  | No. | 1 for Each Type
| 3.1.17 | Pre-stressed non-return valve (PNRV) |  | No. | 1
| 3.1.18 | Gaskets |  | Set | 1
Relevant Peripheral Material (as spare)
| 3.1.19 | Transformer Oil |  | Drum | 10% of total of one transformer oil volume
| 3.1.20 | Silicagel |  | Kg | Equal to the quantity of the first filling
Main Equipment
| 3.2 | Fire Protection Standard Nitrogen Injection and Oil Evacuation System (NIFPS) with all required accessories, panels and instruments |  | No. | 2
Mandatory Spare Parts
| 3.2.1 | Required equipment and accessories mentioned in item 3.2 |  | % | 20%
Main Equipment
| 3.3 | Online Condition Monitoring System with all required accessories and instruments |  | No. | 2
| 3.4 | Surge arrester (1-phase), installed in the Auto TR. 11kV cable box |  | No. | 6
Mandatory Spare
| 3.4.1 | Surge arrester (1-phase), installed in the Auto TR. 11kV cable box |  | No. | 1
TOTAL PRICE ITEM 3
TOTAL PRICE ITEM 3_Spare Parts
| 4 | EARTHING & AUXILIARY TRANSFORMER
Main Equipment
| 4.1 | Earthing & Auxiliary transformer (3-phase units) HV11/LV0.415kV, 500KVA including HV/LV Bushing CT's and all accessories as required |  | No. | 2
Mandatory Spare Parts
| 4.1.1 | Oil Directed Pressure Relief Device |  | No. | 1
| 4.1.2 | Buchholz Relay |  | No. | 1
| 4.1.3 | Oil Level Indicator |  | No. | 1
| 4.1.4 | Winding Temperature Indicator |  | No. | 1
| 4.1.5 | Oil Temperature Indicator |  | No. | 1
| 4.1.6 | Gaskets |  | Set | 1
Main Equipment
| 4.2 | 50 kg wheeled Dry-Powder Fire extinguisher for Auxiliary transformer |  | No. | 2
TOTAL PRICE ITEM 4
TOTAL PRICE ITEM 4_Spare Parts
Main Equipment
| 5 | NEUTRAL EARTHING RESISTOR
| 5.1 | Neutral Earthing Resistor with associated CTs (acc. To SLD) |  | No. | 2
TOTAL PRICE ITEM 5
| 6 | 400kV PROTECTION SYSTEMS
Main Equipment
| 6.1 | 400kV OHL Protection System including:
| 6.1.1 | Main1 21L Protection Relay (with all required functions as per PSLD) |  | No. | 4
Mandatory Spare
| 6.1.1.1 | Main1 21L Protection Relay (with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 6.1.2 | Main2 87L Protection Relay (with all required functions as per PSLD) |  | No. | 4
Mandatory Spare
| 6.1.2.1 | Main2 87L Protection Relay (with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 6.1.3 | Auto-Reclose Relay (with all required functions and Voltage Selection Logic as per PSLD) |  | No. | 4
| 6.1.4 | Point On Wave (POW) Switching relay (Synchronous Switching Controller) (with required Voltage Selection Logic As per PLSD) |  | No. | 10
Main Equipment
| 6.1.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. |  | Lot | 1
Mandatory Spare Parts
| 6.1.5.1 | All accessories mentioned in item 6.1.5 |  | % | 20%
Main Equipment
| 6.1.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 8
Mandatory Spare Parts
| 6.1.6.1 | All panel accessories acc. to item 6.1.6 |  | % | 20%
Required Equipment
| 6.1.7 | All required equipment for modification works in remote Existing Isinya and Suswa substations, differential relays settings and etc. |  | Lot | 1
Main Equipment
| 6.2 | 400kV HV Transformer Protection System including:
| 6.2.1 | Main 87T+87N Protection (with all required functions as per PSLD) |  | No. | 2
Mandatory Spare
| 6.2.1.1 | Main 87T+87N Protection (with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 6.2.2 | Backup 50/51(N) Protection (with all required functions as per PSLD) |  | No. | 2
Mandatory Spare
| 6.2.2.1 | Backup 50/51(N) Protection (with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 6.2.3 | 87HVC Connection Protection (with all required functions as per PSLD) |  | No. | 2
| 6.2.4 | Earth Fault 50N/51N (SBEF) Protection (with all required functions as per PSLD) |  | No. | 2
| 6.2.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. |  | Lot | 1
Mandatory Spare Parts
| 6.2.5.1 | All accessories mentioned in item 6.2.5 |  | % | 20%
Main Equipment
| 6.2.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 4
Mandatory Spare Parts
| 6.2.6.1 | All panel accessories acc. to item 6.2.6 |  | % | 20%
Main Equipment
| 6.3 | 400kV Distributed type Busbar Protection System, including:
| 6.3.1 | Busbar Protection Relay central module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) |  | No. | 2
| 6.3.2 | Busbar Protection Relay bay module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) |  | No. | 8
Mandatory Spare Parts
| 6.3.3 | Busbar Protection Relays bay module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) |  | No. | 2
Main Equipment
| 6.3.4 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux. relays, test and terminal blocks, timers, wiring etc. to make the system complete |  | No. | 2
Mandatory Spare Parts
| 6.3.4.1 | All panel accessories acc. to item 6.3.2 |  | % | 20%
Main Equipment
| 6.4 | All other equipment required for completion of the 400kV protection system which have not been mentioned in the above rows Speicificly. |  | Lot | 1
TOTAL PRICE ITEM 6
TOTAL PRICE ITEM 6_Spare Parts
| 7 | 220KV PROTECTION SYSTEMS
Main Equipment
| 7.1 | 220kV OHL Protection System including:
| 7.1.1 | Main1 87L Protection (with all required functions as per PSLD) |  | No. | 2
Mandatory Spare
| 7.1.1.1 | Main1 87L Protection (with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 7.1.2 | Main 2 87L Protection (with all required functions as per PSLD) |  | No. | 2
Mandatory Spare
| 7.1.2.1 | Main 2 87L Protection (with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 7.1.3 | Auto-Reclose Relay (with all required functions and Voltage Selection Logic as per PSLD) |  | No. | 2
| 7.1.4 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; end fault; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. |  | Lot | 1
Mandatory Spare Parts
| 7.1.4.1 | All accessories mentioned in item 7.1.4 |  | % | 20%
Main Equipment
| 7.1.5 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 4
Mandatory Spare Parts
| 7.1.5.1 | All panel accessories acc. to item 7.1.5 |  | % | 20%
Main Equipment
| 7.1.6 | Modification works in remote Existing Kimuka substation, differential relays settings and etc. |  | Lot | 1
| 7.2 | 220kV LV Transformer Protection System including:
| 7.2.1 | Backup 67/67(N) Protection(with all required functions as per PSLD) |  | No. | 2
Mandatory Spare
| 7.2.1.1 | Backup 67/67(N) Protection(with all required functions as per PSLD) |  | No. | 1
Main Equipment
| 7.2.2 | 87LVC Connection Protection (with all required functions as per PSLD) |  | No. | 2
| 7.2.3 | Tertiary Winding 50TV/51TV (N) Overcurrent Protection(with all required functions as per PSLD) |  | No. | 2
| 7.2.4 | Earthing Transformer 87NTV 11kV side (with all required functions as per PSLD) |  | No. | 2
| 7.2.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. |  | Lot | 1
Mandatory Spare Parts
| 7.2.5.1 | All accessories mentioned in item 7.2.5 |  | % | 20%
Main Equipment
| 7.2.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 4
Mandatory Spare Parts
| 7.2.6.1 | Mandatory Spare of item 7.2.6 |  | % | 20%
Main Equipment
| 7.3 | 220kV Busbar Distributed Type Protection System, including:
| 7.3.1 | 220kV Busbar Protection Relay central module ACC. To PSLD drawing |  | No. | 2
| 7.3.2 | 220kV Busbar Protection Relay bay modules ACC. To PSLD drawing |  | No. | 4
Mandatory Spare Parts
| 7.3.3 | 220kV Busbar Protection Relay bay module ACC. To PSLD drawing |  | No. | 1
Main Equipment
| 7.3.4 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete |  | No. | 2
Mandatory Spare Parts
| 7.3.4.1 | All panel accessories acc. to item 7.3.2 |  | % | 20%
| 7.4 | Power Transformer Automatic Voltage Regulation including:
| 7.4.1 | Automatic Voltage Regulator Relay |  | No. | 2
Mandatory Spare
| 7.4.1.1 | Automatic Voltage Regulator Relay |  | No. | 1
Main Equipment
| 7.4.2 | Panels with all accessories and auxiliaries, lighting, heating, socket, push buttons, wiring, terminals, test facilities, discrepancy and all other switches, labels, unit measurement indicating lamps, position indicators, alarm announciators, temperature indicators, test block/plug , Labels, etc. and with the following equipment. |  | No. | 2
Mandatory Spare Parts
| 7.4.2.1 | All panel accessories acc. to item 7.4.2 |  | % | 20%
Main Equipment
| 7.5 | All other equipment required for completion of the 220kV protection system which have not been mentioned in the above rows Speicificly. |  | Lot | 1
TOTAL PRICE ITEM 7
TOTAL PRICE ITEM 7_Spare Parts
| 8 | 400/220kV SUBSTATION AUTOMATION and CONTROL SYSTEM
Main Equipment
| 8.1 | All software and licenses |  | Lot | 1
| 8.2 | Bay Control Units (BCU) (with all required functions as per PSLD) |  | No. | 16
Mandatory Spare Parts
| 8.2.1 | Bay Control Units (BCU) (with all required functions as per PSLD) |  | No. | 4
Main Equipment
| 8.3 | Bay Control Panels |  | No. | 6
| 8.4 | Auxiliary and Common Services Bay Control Unit |  | Lot | 1
| 8.5 | Auxiliary and Common Services Panel including all accessories |  | Lot | 1
| 8.6 | PRP communication Station level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) |  | Lot | 1
| 8.7 | PRP communication Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) |  | Lot | 1
Mandatory Spare Parts
| 8.7.1 | LAN Switches (Ports, Star-Coupler, Fibre Optic Cables etc.) |  | % | 20%
Main Equipment
| 8.8 | Substation Computer (server) |  | No. | 2
| 8.9 | Operator Work Station with all required peripherals and monitor |  | Lot | 2
| 8.10 | Engineering Work Station with all required peripherals and monitor |  | No. | 1
| 8.11 | Gateway, Converter, Modem and firewall and all other required equipment. |  | No. | 2
| 8.12 | GPS, Tiem Server, GPS Antenna and all other required equipment. |  | No. | 1
| 8.13 | SOE Printer |  | No. | 1
| 8.14 | Station Log Printer |  | No. | 1
| 8.15 | General Purpose Printer |  | No. | 1
TOTAL PRICE ITEM 8
TOTAL PRICE ITEM 8_Spare Parts
| 9 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
Main Equipment( Existing 220/66 kV Kimuka)
| 9.1 | Differential protection relays with all required accessories (to be installed instead of existing distance relays of Suswa and Isinya lines) |  | No. | 2
TOTAL PRICE ITEM 9
| 10 | TELECOMMUNICATION & NCC/RCC/NSCC
Main Equipment
| 10.1 | New Telecommunication and SDH System for 400/220kV Substation including:
| 10.1.1 | Panel (800*600*2260mm) with all required accessories |  | No. | 1
| 10.1.2 | Basic modules are included: Backplane, Main controler, Supply board, etc. |  | No. | 1
| 10.1.3 | Optical Interface Board STM-16 (2*ports) |  | No. | 3
| 10.1.4 | SFP Moudule |  | No. | 6
| 10.1.5 | E1 Interface Board |  | No. | 2
| 10.1.6 | FE Interface Board (SCADA) |  | No. | 1
| 10.1.7 | FE Interface Board (Office LAN) |  | No. | 1
| 10.1.8 | 2- Wire telephone Interface Board |  | No. | 1
| 10.1.9 | RS-232 Data Board |  | No. | 1
| 10.1.10 | Protection Interface Board for Differential protection relay (4 ports supposed for each card) OPIC card |  | No. | 6
| 10.1.11 | Protection Interface Board for Distance (4 ports supposed for each card) TEPI cards |  | No. | 4
Mandatory Spare Parts
| 10.1.11.1 | Telecommunication TEPI card (4 ports supposed for each card) |  | No. | 1
Main Equipment
| 10.2 | New Firewall system with all necessary Licenses |  | Lot | 1
| 10.3 | New IP phone Equipment with licences, switches, etc. (at least 2x indoor & 2x outdoor) for Kimuka 400/220kV substation
| 10.3.1 | Phone set |  | No. | 4
| 10.3.2 | Telephone Junction Box |  | Lot | 1
| 10.3.3 | LAN Cable |  | Lot | 1
| 10.3.4 | Outdoor Cabin |  | No. | 2
Mandatory Spare Parts
| 10.3.5 | Mandatory Spare for New IP phone Equipment (Indoor/Outdoor) including: Power Supply,Patch cord,Head set,Head set cord, Wall mount kit, Expansion Moudle ... etc. |  | Lot | 1
Main Equipment
| 10.4 | Required equipment for modification works at existing Kimuka 220/66kV substation;
| 10.4.1 | Required equipment for modification works at existing Telecommunication and SDH System in 220/66kV Substation |  | Lot | 1
| 10.4.2 | Required equipment for modification works at existing Teleprotection Signalling Equipment in 220/66kV Substation |  | Lot | 1
| 10.5 | Required equipment for modification works at existing Suswa 400/220 KV substation;
| 10.5.1 | Required equipment for modification works at existing Telecommunication and SDH System in Suswa 400/220 KV substation included: |  | Lot | 1
| 10.5.2 | Required equipment for modification works at existing Teleprotection Signalling Equipment in existing Suswa 400/220 KV substation |  | Lot | 1
| 10.6 | Required equipment for modification works at existing Isinya 400 KV substation;
| 10.6.1 | Required equipment for modification works at existing Telecommunication and SDH System in existing Isinya 400 KV substation |  | Lot | 1
| 10.6.2 | Required equipment for modification works at existing Teleprotection Signalling Equipment in existing existing Isinya 400 KV substation |  | Lot | 1
| 10.7 | Required equipment for incorporating new and existing substation's signals into the SCADA/EMS System at the NCC/RCC/NSCC |  | Lot | 1
| 10.8 | Required equipment for modifications to NCC/RCC/NSCC mimic board (if any) |  | Lot | 1
| 10.9 | Required equipment fo modification works at existing PABX in Lessos RCC including all necessary Licenses, Network switches and any other facilities for communication with NCC, RCC and NSCC |  | Lot | 1
| 10.10 | All necessary licences, hardware, software and configuration needed for the existing network management system (NMS) to create the STM-16 link that forms part of the backbone network from Kimuka 400/220kV Substation and other Substations to the NCC/RCC/NSCC |  | Lot | 1
| 10.11 | Required equipment and accessories for interconnection between the OPGW and fibre optic cable in communication room & communication collocation room
| 10.11.1 | Optical Distribution panel (Main & Collocation Communication room) |  | Set | 2
| 10.11.2 | Optical Distribution Unit (OCDF) for 48 cores fiber ( Main Communication romm) |  | Set | 5
| 10.11.3 | Digital Distribution Unit (ODF) for 48 cores fiber |  | Set | 5
| 10.11.4 | Tail Optical Fiber |  | Lot | 1
| 10.11.5 | 48 Core Steel Tape Armoured Outdoor Optical Fiber GYXTW |  | Lot | 1
| 10.11.6 | Coaxial Cable |  | Lot | 1
| 10.11.7 | PVC Pipe suitable for the distance between entry gantry and communication room |  | Lot | 1
| 10.11.8 | Optical Cable plane |  | Lot | 1
| 10.11.9 | Steel Tube from junction box to entry of cable channel |  | Lot | 1
| 10.11.10 | OPGW Splice Closures joint box with all accessories |  | Set | 3
| 10.12 | EPABX system for communication between guard house and individual Staff housings including:
| 10.12.1 | Exchange |  | Lot | 1
| 10.12.2 | Telephone equipment |  | No. | 16
| 10.12.3 | Junction boxes |  | Lot | 1
| 10.12.4 | Cabling |  | Lot | 1
| 10.12.5 | Power supply with backup battery |  | Lot | 1
Main Equipment
TOTAL PRICE ITEM 10
TOTAL PRICE ITEM 10_Spare Parts
| 11 | LV CABLES AND ACCESSORIES
Main Equipment
| 11.1 | Auxiliary power and control cabling including single and three-phase power cables, control cables required for control, protection, metering and alarms, CTs' and CVTs' circuit cabes, DC supply cables. |  | Lot | 1
Mandatory Spare Parts
| 11.1.1 | All types of cables mentioned in item 11.1. |  | % | 10%
Main Equipment
| 11.2 | Substation internal fibre optic cabling, coaxilal cables. |  | Lot | 1
Mandatory Spare Parts
| 11.2.1 | All types of cables mentioned in item 11.2. |  | % | 10%
Main Equipment
| 11.3 | Cable laying equipment including cable trays, ladders, supports & fixing calmps, glands, lugs, terminals, rails, labels, cable shoes, accessories, fire proof sealing of ducts/conduits/openings, and etc. |  | Lot | 1
Mandatory Spare Parts
| 11.3.1 | Cable laying equipment acc. to item 11.3. |  | % | 10%
TOTAL PRICE ITEM 11
TOTAL PRICE ITEM 11_Spare Parts
| 12 | EARTHING & LIGHTNING PROTECTION
| 12.1 | Earthing system (including main earth grid, earth mat, rizer, bonding, connector, clamp, fitting, earth rod and well, inspection earth pits etc. as required) |  | Lot | 1
| 12.2 | Lightning protection system (including shield wire, air termination rod, down conductor, equipotential bonding, disconnecting link, etc. as required) |  | Lot | 1
TOTAL PRICE ITEM 12
| 13 | 11KV CABLE SYSTEM
Main Equipment
| 13.1 | 11kV cables for connection between A.TR. and Auxiliary & Earthng Transformer |  | Lot | 1
Mandatory Spare Parts
| 13.1.1 | 11kV cables for connection between A.TR. and Auxiliary & Earthng Transformer |  | Lot | 1 run (eq. to distance between A.TR. & EAT)
Main Equipment
| 13.2 | Cable laying equipment including, cable trays, ladders, supports & fixing calmps, accessories, glands, lugs, terminals, rails, labels, cable shoes, fire proof sealing of ducts/conduits/openings etc. |  | Lot | 1
| 13.3 | 11kV cable sealing end (CSE) for 11kV side of 200MVA Auto-Transformers and HV side of Auxiliary & Earthing Transformer |  | No. | 12
Mandatory Spare Parts
| 13.3.1 | 11kV cable sealing end (CSE) for 11kV side of 200MVA Auto Transformers and HV side of Auxiliary & Earthing Transformer |  | No. | 1
TOTAL PRICE ITEM 13
TOTAL PRICE ITEM 13_Spare Parts
| 14 | SUPPORT STRUCTURES
Main Equipment
| 14.1 | Steel supports for 400kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
| 14.2 | Steel supports for 220kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
| 14.3 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchor bolts, plates and etc.) |  | Lot | 1
| 14.4 | Miscellaneous structures for interconnecting 400kV and 220kV switchyards (including all the required hot dip galvanised steel, bolts, nuts, anchor bolts, plates and etc.) |  | Lot | 1
| 14.5 | Structures for installing batteries (including all the required anti-acid hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) |  | Lot | 1
TOTAL PRICE ITEM 14
| 15 | AUXILIARY SUPPLY
Main Equipment
| 15.1 | LVAC system
| 15.1.1 | AC Main and distribution panels, AC distribution outdoor cubicles, fuse box for oil treatment socket with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | No. | 6
| 15.1.2 | Oil treatment panel and accessories (including heavy duty outlet socket, fuses, glands, etc.) |  | No. | 2
| 15.1.3 | AC distribution panels in BCR, with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | No. | 6
| 15.1.4 | Solar PV Modules, Charge Controllers, Hybrid Inverters and Batteries for Outdoor and Indoor lighting and associated panels/switchgears and accessories |  | Lot | 1
Mandatory Spare Parts
| 15.1.4 | Equipment and accessories mentioned in item 15.1.1, 15.1.2, 15.1.3,15.1.4 |  | % | 20%
Main Equipment
| 15.2 | 110VDC system
| 15.2.1 | 110Vdc Main and distribution panels, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | No. | 5
| 15.2.2 | 110Vdc distribution panels in BCR, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | No. | 6
| 15.2.3 | 110Vdc battery chargers with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | Sets | 2
| 15.2.4 | 110Vdc batteries with structures/frames with all accessories (including Connection Bars, Cables, Luges, Bolts, Nuts, Washers, anti-Acid covers, Themometer, Density Meter, tools for battery filling and etc.) |  | Sets | 2
Mandatory Spare Parts
| 15.2.5 | Equipment, accessories and material mentioned in item 15.2.1, 15.2.2, 15.2.3, 15.2.4 |  | % | 20%
Main Equipment
| 15.3 | 48VDC system
| 15.3.1 | 48Vdc distribution panel, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | No. | 3
| 15.3.2 | 48Vdc battery chargers with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) |  | Sets | 2
| 15.3.3 | 48Vdc batteries with structures/frames with all accessories (including Connection Bars, Cables, Luges, Bolts, Nuts, Washers, anti-Acid covers, Themometer, Density Meter, tools for battery filling and etc.) |  | Sets | 2
Mandatory Spare Parts
| 15.3.4 | Equipment, accessories and material mentioned in item 15.3.1, 15.3.2, 15.3.3 |  | % | 20%
Main Equipment
| 15.4 | 415V ac Uninterruptible Power Supply including isolating by-pass transformers, inverters, static switch, manual bypass switch, panels & distribution boards |  | Sets | 2
Mandatory Spare Parts
| 15.4.1 | Equipment and accessories mentioned in item 15.4 |  | % | 20%
Main Equipment
| 15.5 | Main Diesel Generator 500kVA including generator control and protection panel and all peripheral equipment, reservior(s), and accessories. |  | Set | 1
Mandatory Spare Parts
| 15.5.1 | Mechanical, Electrical & Control Equipment/Accessories of Diesel Generator |  | % | 20%
Main Equipment
| 15.6 | Diesel Generator 200kVA including generator control and protection panel and all peripheral equipment, reservior(s), and accessories for Technical and Security Staff Housing |  | Set | 1
Mandatory Spare Parts
| 15.6.1 | Mechanical, Electrical & Control Equipment/Accessories of Diesel Generator |  | % | 20%
TOTAL PRICE ITEM 15
TOTAL PRICE ITEM 15_S]pare Parts
| 16 | TARIFF METERING
Main Equipment
| 16.1 | Tariff metering system for 400kV OHL, complete with wiring, accessories and etc. including:
| 16.1.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 4
| 16.1.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 4
Mandatory Spare Parts
| 16.1.2.1 | Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 2
Main Equipment
| 16.2 | Tariff metering system for 220kV OHL feeders, complete with wiring, accessories etc. and including:
| 16.2.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 2
| 16.2.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 2
Mandatory Spare Parts
| 16.2.2.1 | Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 1
Main Equipment
| 16.3 | Tariff metering system for Auto-Transformer, complete with wiring, accessories etc. and including:
| 16.3.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 2
| 16.3.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 2
Mandatory Spare Parts
| 16.3.2.1 | Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 1
Main Equipment
| 16.4 | Tariff metering system for LVAC incomer panels, complete with wiring, accessories etc. and including:
| 16.4.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy |  | No. | 2
| 16.5 | Metering data collection and communication system, complete with fibre optic cabling, accessories, each kind of energy meters software and communication ports. All media and accessories in order to transferring energy meter measured values to remote center according to both KETRACO and KPLC required specification. |  | Lot | 1
Mandatory Spare Parts
| 16.5.1 | Required accessories for item 16.4 |  | % | 20%
Main Equipment
| 16.6 | Metering panel with all accessories and auxiliaries, lighting, heating, socket, wiring, terminals, test facilities, and all other switches, labels, test block/plug , Labels, etc. |  | No. | 3
Mandatory Spare Parts
| 16.6.1 | Required accessories for item 16.5 |  | % | 20%
Main Equipment
| 16.7 | All other related relays, racks, Voltage/Current test block, cubicles, terminals, As needed to complete the metering system. |  | Lot | 1
Mandatory Spare Parts
| 16.7.1 | Required accessories for item 16.6 |  | % | 20%
TOTAL PRICE ITEM 16
TOTAL PRICE ITEM 16_Spare Parts
| 17 | FAULT MONITORING SYSTEM & PMU
Main Equipment
| 17.1 | Fault and Event Monitoring System |  | Lot | 1
| 17.2 | Phasor Mesurment Unit (PMU) system with Separate GPS, Ethernet Switch, Industrial PC |  | Lot | 1
Mandatory Spare Parts
| 17.2.1 | Required accessories for item 17.1 and 17.2 |  | % | 20%
Main Equipment
| 17.3 | Data Aquisition Units |  | Lot | 1
| 17.4 | Master Station |  | No. | 1
| 17.5 | Local HMI |  | No. | 1
| 17.6 | Fault and Event Recorder Panel with all accessories such as wiring, Lighting, heater, socket, terminal, Indication lamp, transducer, control equipment, monitor, keyboard, mouse, case, printer, I/O card and etc.(all requirements for future extension must be considered) |  | Lot | 1
Mandatory Spare Parts
| 17.6.1 | Required accessories for item 17.6 |  | % | 20%
Main Equipment
| 17.7 | Phasor Mesurment Unit Panel with all accessories such as wiring, Lighting, heater, socket, terminal, Indication lamp, transducer, control equipment, monitor, keyboard, mouse, case, printer, I/O card and etc.(all requirements for future extension must be considered) |  | Lot | 1
Mandatory Spare Parts
| 17.7.1 | Required accessories for item 17.7 |  | % | 20%
TOTAL PRICE ITEM 17
TOTAL PRICE ITEM 17_Spare Parts
| 18 | MISCELLANEOUS
Main Equipment
| 18.1 | Bay Marshalling Kiosk |  | Lot | 1
| 18.2 | CCTV System with all ralated equipment for indoor and outdoor, including Cameras of suitable type and required specifications with poles, recorder, storage, monitor, switch, cabling, boxes, fixings, brackets and etc. (acc. to technical specifications in part 2-B) |  | Lot | 1
Mandatory Spare Parts
| 18.2.1 | Required accessories for item 18.2 |  | % | 20%
| 18.3 | Padlocks / Keys (for panels, outdoor equipments, doors, etc.) |  | Lot | 1
| 18.4 | Equipment/Bay labels, safety warning plates, road signages, room name plates, etc. |  | Lot | 1
Main Equipment
| 18.5 | Tools and Appliances as stated in Part 2-A clause 19 of the Employer's Requirements |  | Lot | 1
| 18.6 | Tools and Equipment as stated in part 2-A clause 20 listed A-R, of the Employers Requirements (Bidder shall submit relevant itemized list with quantity, description and breackdown price) |  | Lot | 1
| 18.6.1 | Gas handling trolley |  | Lot | 1
| 18.6.2 | 400kV Portable Earth including Leads, chopsticks,cable, earting rods, connectors and clamps, etc. |  | Set | 2
| 18.6.3 | 220kV Portable Earth including Leads, Chopsticks, cable, earting rods, connectors and clamps, etc. |  | Set | 2
| 18.6.4 | Project Laptops with all required software as per Client's requirmenets in Part 2-A, |  | No. | 8
| 18.6.5 | Rugged/Industrial Laptop for substation protection and control system (CRP/SAS) with all required softwareas, as per Client's requirmenets in Part 2-A, |  | No. | 2
| 18.6.6 | Softwares and Licences as listed below and as per Part 2A AutoCAD for windows STAAD Pro DIgSILENT DIALux BIM software |  | Lot | 1
| 18.7 | Forklift for storage warehouse |  | No. | 1
TOTAL PRICE ITEM 18
TOTAL PRICE ITEM 18_Spare Parts
| 19 | Site Transport as per Employer's Requirements, Part 2-A, Clause 32
Main Equipment
| 19.1 | Vehicles as per part 2-A, Clause 32
| 19.1.1 | Vehicle Type 2 as per Part 2-A |  | No. | 6
| 19.1.2 | Vehicle Type 3 as per Part 2-A |  | No. | 3
TOTAL PRICE ITEM 19
TOTAL PRICE SCHEDULE 1A KIMUKA SUBSTATION Note: Contractor shall include all equipment and materials in his proposal, which are necessary to complete the works.
TOTAL PRICE SCHEDULE 1A KIMUKA SUBSTATION_Spare Parts
Note on G10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease delete currencies. Because the bidder can offer in any currency Reply: deleted
Note on C60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please provide quantity Reply: Since the design is on the contractor 10% spare is considered sufficient
Note on C64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please provide quantity Reply: Since the design is on the contractor 10% spare is considered sufficient
Note on C86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease define busbar type either tubular type or conductor. Please see comments in the related parts about the type of busbar Reply: Please note that both tubular and stranded conductors can be used , hence the bidder will fill which is relevant
Note on C90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: for what??? please address the clause number in the Employer’s Requirement Reply: Stranded conductor is for normal connection between equipment as well as can be used also for busbar as per bidder's design
Note on C111: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease see comments in 400 kV primary plant Reply: Response provided
Note on C653: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease separate solar PV system Reply: This is to be considered a complete system hence separation is not recommended
Note on C779: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please list, or address the clause no Reply: Amended
Note on C793: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Software and licences can be considered in Schedule 3. Please contact WB’s procurement specialist about purchasing of these softwares and licences Reply: Schedule 3 is only for design services whereas these licenses are to be procured and installed
Note on C795: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please list the items to avoid any misunderstanding Reply: Deleted
Note on C799: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It is subjective. Please delete. Reply: Agreed

## Schedule 2A_SS
SCHEDULE NO. 2A
PLANT, EQUIPMENT AND MANDATORY SPARE PARTS SUPPLIED FROM WITHIN THE CLIENT'S COUNTRY
FOR KIMUKA SUBSTATION
Note 1:All proposed mandatory spare parts for each equipment or system shall be specified in detail by Bidders.
Note 2: All main and spare equipment shall be provided for proper operation in four altitude categories (to optimize main equipment/ spare parts and achieve interchangeability at country level), including 1000, 1500, 2000 and 2500 meter above sea level. In case of other range may has been mentioned in the schedules of technical information (Part 2-E), the higher altitude category shall be considered.
Note 3: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
| 1 | 2 | 3 | 4 | 5 | 6
| Item No | Description | Unit | Estimated Quantity | Local Currency (KSh) = KENYAN SHILLINGS | Total Price
[5 empty] | Local Manufacture | Local Manufacture
[5 empty] | Unit Price (DAP) | (Quantity x Unit Price)
[5 empty] | KSh | KSh
| 1 | 400kV PRIMARY PLANT
Main Equipment
| 1.1 | Circuit Breaker single pole operated, 3 phase | No. | 10
Relevant Mandatory Spare Parts
| 1.1.1 | Trip coil | No. | 3
| 1.1.2 | Close coil | No. | 2
| 1.1.3 | Anti pumping relay | No. | 1
| 1.1.4 | Density blocking relay | No. | 1
| 1.1.5 | Density meter | No. | 1
| 1.1.6 | Heater | No. | 2
| 1.1.7 | Motor for operating mechanism | No. | 1
| 1.1.8 | Complete pole including fixed and moving contacts, pull rod, etc. | No. | 3
Relevant Peripheral Devices/Material
| 1.1.9 | Gas filling devices | No. | 1
| 1.1.10 | SF6 gas | % | 20% of required volume for first filling of CBs
| 1.1.11 | SF6 gas leakage detector | No. | 1
Main Equipment
| 1.2 | Motorized Disconnector (3-phase), complete with one integral motorised earth switch, and earth mat | No. | 20
Relevant Mandatory Spare Parts
| 1.2.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-ES (3-phase) | No. | 2
| 1.2.2 | Motorized operating mechanism suitable for DS-ES | No. | 2
Main Equipment
| 1.3 | Motorized Disconnector (3-phase), complete with two integral motorised earth switches and earth mat | No. | 6
Relevant Mandatory Spare Parts
| 1.3.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-2ES (3-phase) | No. | 1
| 1.3.2 | Motorized operating mechanism suitable for DS-2ES | No. | 1
Main Equipment
| 1.4 | Motorized Earthing switch (3-phase), with earth mat | No. | 2
| 1.5 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 18
Relevant Mandatory Spare
| 1.5.1 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 2
Main Equipment
| 1.6 | Post insulator | Lot | 1
Relevant Mandatory Spare
| 1.6.1 | Post insulator of all types | % | 10%
Main Equipment
| 1.7 | Insulator string (Suspension and Strain types with harware fitting) | Lot | 1
Relevant Mandatory Spare
| 1.7.1 | Insulator string of all types (Suspension and Strain types with harware fitting) | % | 10%
Main Equipment
| 1.8 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) | No. | 30
Relevant Mandatory Spare
| 1.8.1 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) | No. | 3
Main Equipment
| 1.9 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 12
Relevant Mandatory Spare
| 1.9.1 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 1
Main Equipment
| 1.10 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) | No. | 12
Relevant Mandatory Spare
| 1.10.1 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) | No. | 1
Main Equipment
| 1.11 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) | No. | 12
Relevant Mandatory Spare
| 1.11.1 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) | No. | 1
Main Equipment
| 1.12 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) | No. | 12
Relevant Mandatory Spare
| 1.12.1 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) | No. | 1
Main Equipment
| 1.13 | Tubular Conductor | Lot | 1
Relevant Mandatory Spare
| 1.13.1 | Tubular Conductor of all types | % | 10%
Main Equipment
| 1.14 | Stranded Conductor | Lot | 1
Relevant Mandatory Spare
| 1.14.1 | Stranded Conductor of all types | % | 10%
Main Equipment
| 1.15 | Connectors and Clamps for Tubular Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
Relevant Mandatory Spare
| 1.15.1 | Connectors and Clamps for Tubular Conductors of all types (together with stainless steel nuts, bolts, bimetal) | % | 10%
Main Equipment
| 1.16 | Connectors and Clamps for Stranded Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
Relevant Mandatory Spare
| 1.16.1 | Connectors and Clamps for Stranded Conductors of all types (together with stainless steel nuts, bolts, bimetal) | % | 10%
Main Equipment
| 1.17 | Online monitoring system for 400kV Circuit Breaker | No. | 10
Remote End Substation_ISINYA
| 1.18 | All required material such as conductors, fittings , connectord and calmps and etc as required regarding to connection of the 400kV Suswa-1 to switchyard 400kV with completion the connection between of the feeder's equipment as per scope of work | No. | 10
TOTAL PRICE ITEM 1
TOTAL PRICE ITEM 1_Spare Parts
| 2 | 220kV PRIMARY PLANT
Main Equipment
| 2.1 | Circuit breaker single pole operated, 3 phase | No. | 6
Relevant Mandatory Spare Parts
| 2.1.1 | Trip coil | No. | 3
| 2.1.2 | Close coil | No. | 1
| 2.1.3 | Anti pumping relay | No. | 1
| 2.1.4 | Density blocking relay | No. | 1
| 2.1.5 | Density meter | No. | 1
| 2.1.6 | Heater | No. | 2
| 2.1.7 | Motor for operating mechanism | No. | 1
| 2.1.8 | Complete pole including fixed and moving contacts, pull rod, etc. | No. | 1
Relevant Peripheral Devices/ Material
| 2.1.9 | Gas filling devices | No. | 1
| 2.1.10 | SF6 gas | % | 20% of required volume for first filling of CBs
| 2.1.11 | SF6 gas leakage detector | No. | 1
Main Equipment
| 2.2 | Motorized Disconnector (3-phase), complete with one integral motorised earth switch, and earth mat | No. | 12
Relevant Mandatory Spare Parts
| 2.2.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-ES (3-phase) | No. | 1
| 2.2.2 | Motorized operating mechanism suitable for DS-ES | No. | 1
Main Equipment
| 2.3 | Motorized Disconnector (3-phase), complete with two integral motorised earth switches and earth mat | No. | 4
Relevant Mandatory Spare Parts
| 2.3.1 | Complete pole which includes current carrying parts, insulators, fixing parts and earthing switch suitable for DS-2ES (3-phase) | No. | 1
| 2.3.2 | Motorized operating mechanism suitable for DS-2ES | No. | 1
Main Equipment
| 2.4 | Motorized Earthing switch (3-phase), with earth mat | No. | 2
| 2.5 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 12
Relevant Mandatory Spare Parts
| 2.5.1 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 1
Main Equipment
| 2.6 | Post insulator | Lot | 1
Relevant Mandatory Spare Parts
| 2.6.1 | Post insulator of all types | % | 10%
Main Equipment
| 2.7 | Insulator string (Suspension and Strain types with harware fitting) | Lot | 1
Relevant Mandatory Spare Parts
` | 2.7.1 | Insulator string of all types (Suspension and Strain types with harware fitting) | % | 10%
Main Equipment
| 2.8 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) | No. | 18
Relevant Mandatory Spare Parts
| 2.8.1 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) | No. | 2
Main Equipment
| 2.9 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 6
Relevant Mandatory Spare Parts
| 2.9.1 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 1
Main Equipment
| 2.10 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 6
Relevant Mandatory Spare Parts
| 2.10.1 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 1
Main Equipment
| 2.11 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) | No. | 12
Relevant Mandatory Spare Parts
| 2.11.1 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) | No. | 1
Main Equipment
| 2.12 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) | No. | 6
Relevant Mandatory Spare Parts
| 2.12.1 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) | No. | 1
Main Equipment
| 2.13 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) | No. | 6
Relevant Mandatory Spare Parts
| 2.13.1 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) | No. | 1
Main Equipment
| 2.14 | Tubular Conductor | Lot | 1
Relevant Mandatory Spare Parts
| 2.14.1 | Tubular Conductor of all types | % | 10%
Main Equipment
| 2.15 | Stranded Conductor | Lot | 1
Relevant Mandatory Spare Parts
| 2.15.1 | Stranded Conductor of all types | % | 10%
Main Equipment
| 2.16 | Connectors and Clamps for Tubular Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
Relevant Mandatory Spare
| 2.16.1 | Connectors and Clamps for Tubular Conductors of all types (together with stainless steel nuts, bolts, bimetal) | % | 10%
Main Equipment
| 2.17 | Connectors and Clamps for Stranded Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
Relevant Mandatory Spare
| 2.17.1 | Connectors and Clamps for Stranded Conductors of all types (together with stainless steel nuts, bolts, bimetal) | % | 10%
| 2.18 | Remote End Substation_ISINYA
| 2.18.1 | 220 kV Surge arrester (1-phase) including surge counter and earth leakage meter | No | 3
| 2.18.2 | PI | No | 3
TOTAL PRICE ITEM 2
TOTAL PRICE ITEM 2_Spare Parts
| 3 | AUTO TRANSFORMER (A.TR.)
Main Equipment
| 3.1 | Auto transformer (3-phase units) with tertiary winding HV400/LV220/TV11kV, 200MVA including HV/LV/TV/NV Bushing CT's, OLTC, RTCC,OLCM, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS | No. | 2
Mandatory Spare Parts
| 3.1.1 | Bushing for HV side | No. | 1
| 3.1.2 | Bushing for LV side | No. | 1
| 3.1.3 | Bushing for Neutral H.V. side | No. | 1
| 3.1.4 | Bushing and Insulator for T.V. side | Set | 1
| 3.1.5 | Oil Directed Pressure Relief Device (main tank) | No. | 1
| 3.1.6 | Oil Directed Pressure Relief Device (OLTC) | No. | 1
| 3.1.7 | Buchholz Relay | No. | 1
| 3.1.8 | Oil Level Indicator for Main Tank | No. | 1
| 3.1.9 | Oil Level Indicator for OLTC | No. | 1
| 3.1.10 | Oil Surge Relay for OLTC | No. | 1
| 3.1.11 | Cooling Fans | No. | 4
| 3.1.12 | Winding Temperature Indicator | No. | 1
| 3.1.13 | Oil Temperature Indicator | No. | 1
| 3.1.14 | Valves for Radiators | Set | 1
| 3.1.15 | Contactors and required accessories eg. Aux. Relay, MCB, Control relay, and etc. (in Marshalling Kiosk) | No. | 1 for Each Type
| 3.1.16 | Transducer | No. | 1 for Each Type
| 3.1.17 | Pre-stressed non-return valve (PNRV) | No. | 1
| 3.1.18 | Gaskets | Set | 1
Relevant Peripheral Material (as spare)
| 3.1.19 | Transformer Oil | Drum | 10% of total of one transformer oil volume
| 3.1.20 | Silicagel | Kg | Equal to the quantity of the first filling
Main Equipment
| 3.2 | Fire Protection Standard Nitrogen Injection and Oil Evacuation System (NIFPS) with all required accessories, panels and instruments | No. | 2
Mandatory Spare Parts
| 3.2.1 | Required equipment and accessories mentioned in item 3.2 | % | 20%
Main Equipment
| 3.3 | Online Condition Monitoring System with all required accessories and instruments | No. | 2
| 3.4 | Surge arrester (1-phase), installed in the Auto TR. 11kV cable box | No. | 6
Mandatory Spare
| 3.4.1 | Surge arrester (1-phase), installed in the Auto TR. 11kV cable box | No. | 1
TOTAL PRICE ITEM 3
TOTAL PRICE ITEM 3_Spare Parts
| 4 | EARTHING & AUXILIARY TRANSFORMER
Main Equipment
| 4.1 | Earthing & Auxiliary transformer (3-phase units) HV11/LV0.415kV, 500KVA including HV/LV Bushing CT's and all accessories as required | No. | 2
Mandatory Spare Parts
| 4.1.1 | Oil Directed Pressure Relief Device | No. | 1
| 4.1.2 | Buchholz Relay | No. | 1
| 4.1.3 | Oil Level Indicator | No. | 1
| 4.1.4 | Winding Temperature Indicator | No. | 1
| 4.1.5 | Oil Temperature Indicator | No. | 1
| 4.1.6 | Gaskets | Set | 1
Main Equipment
| 4.2 | 50 kg wheeled Dry-Powder Fire extinguisher for Auxiliary transformer | No. | 2
TOTAL PRICE ITEM 4
TOTAL PRICE ITEM 4_Spare Parts
Main Equipment
| 5 | NEUTRAL EARTHING RESISTOR
| 5.1 | Neutral Earthing Resistor with associated CTs (acc. To SLD) | No. | 2
TOTAL PRICE ITEM 5
| 6 | 400kV PROTECTION SYSTEMS
Main Equipment
| 6.1 | 400kV OHL Protection System including:
| 6.1.1 | Main1 21L Protection Relay (with all required functions as per PSLD) | No. | 4
Mandatory Spare
| 6.1.1.1 | Main1 21L Protection Relay (with all required functions as per PSLD) | No. | 1
Main Equipment
| 6.1.2 | Main2 87L Protection Relay (with all required functions as per PSLD) | No. | 4
Mandatory Spare
| 6.1.2.1 | Main2 87L Protection Relay (with all required functions as per PSLD) | No. | 1
Main Equipment
| 6.1.3 | Auto-Reclose Relay (with all required functions and Voltage Selection Logic as per PSLD) | No. | 4
| 6.1.4 | Point On Wave (POW) Switching relay (Synchronous Switching Controller) (with required Voltage Selection Logic As per PLSD) | No. | 10
Main Equipment
| 6.1.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
Mandatory Spare Parts
| 6.1.5.1 | All accessories mentioned in item 6.1.5 | % | 20%
Main Equipment
| 6.1.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 8
Mandatory Spare Parts
| 6.1.6.1 | All panel accessories acc. to item 6.1.6 | % | 20%
Required Equipment
| 6.1.7 | All required equipment for modification works in remote Existing Isinya and Suswa substations, differential relays settings and etc. | Lot | 1
Main Equipment
| 6.2 | 400kV HV Transformer Protection System including:
| 6.2.1 | Main 87T+87N Protection (with all required functions as per PSLD) | No. | 2
Mandatory Spare
| 6.2.1.1 | Main 87T+87N Protection (with all required functions as per PSLD) | No. | 1
Main Equipment
| 6.2.2 | Backup 50/51(N) Protection (with all required functions as per PSLD) | No. | 2
Mandatory Spare
| 6.2.2.1 | Backup 50/51(N) Protection (with all required functions as per PSLD) | No. | 1
Main Equipment
| 6.2.3 | 87HVC Connection Protection (with all required functions as per PSLD) | No. | 2
| 6.2.4 | Earth Fualt 50N/51N (SBEF) Protection (with all required functions as per PSLD) | No. | 2
| 6.2.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
Mandatory Spare Parts
| 6.2.5.1 | All accessories mentioned in item 6.2.5 | % | 20%
Main Equipment
| 6.2.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 4
Mandatory Spare Parts
| 6.2.6.1 | All panel accessories acc. to item 6.2.6 | % | 20%
Main Equipment
| 6.3 | 400kV Distributed type Busbar Protection System, including:
| 6.3.1 | Busbar Protection Relay central module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) | No. | 2
| 6.3.2 | Busbar Protection Relay bay module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) | No. | 8
Mandatory Spare Parts
| 6.3.3 | Busbar Protection Relays bay module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) | No. | 2
Main Equipment
| 6.3.4 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux. relays, test and terminal blocks, timers, wiring etc. to make the system complete | No. | 2
Mandatory Spare Parts
| 6.3.4.1 | All panel accessories acc. to item 6.3.2 | % | 20%
Main Equipment
| 6.4 | All other equipment required for completion of the 400kV protection system which have not been mentioned in the above rows Speicificly. | Lot | 1
TOTAL PRICE ITEM 6
TOTAL PRICE ITEM 6_Spare Parts
| 7 | 220KV PROTECTION SYSTEMS
Main Equipment
| 7.1 | 220kV OHL Protection System including:
| 7.1.1 | Main1 87L Protection (with all required functions as per PSLD) | No. | 2
Mandatory Spare
| 7.1.1.1 | Main1 87L Protection (with all required functions as per PSLD) | No. | 1
Main Equipment
| 7.1.2 | Main 2 87L Protection (with all required functions as per PSLD) | No. | 2
Mandatory Spare
| 7.1.2.1 | Main 2 87L Protection (with all required functions as per PSLD) | No. | 1
Main Equipment
| 7.1.3 | Auto-Reclose Relay (with all required functions and Voltage Selection Logic as per PSLD) | No. | 2
| 7.1.4 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; end fault; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
Mandatory Spare Parts
| 7.1.4.1 | All accessories mentioned in item 7.1.4 | % | 20%
Main Equipment
| 7.1.5 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 4
Mandatory Spare Parts
| 7.1.5.1 | All panel accessories acc. to item 7.1.5 | % | 20%
Main Equipment
| 7.1.6 | Modification works in remote Existing Kimuka substation, differential relays settings and etc. | Lot | 1
| 7.2 | 220kV LV Transformer Protection System including:
| 7.2.1 | Backup 67/67(N) Protection(with all required functions as per PSLD) | No. | 2
Mandatory Spare
| 7.2.1.1 | Backup 67/67(N) Protection(with all required functions as per PSLD) | No. | 1
Main Equipment
| 7.2.2 | 87LVC Connection Protection (with all required functions as per PSLD) | No. | 2
| 7.2.3 | Tertiary Winding 50TV/51TV (N) Overcurrent Protection(with all required functions as per PSLD) | No. | 2
| 7.2.4 | Earthing Transformer 87NTV 11kV side (with all required functions as per PSLD) | No. | 2
| 7.2.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
Mandatory Spare Parts
| 7.2.5.1 | All accessories mentioned in item 7.2.5 | % | 20%
Main Equipment
| 7.2.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 4
Mandatory Spare Parts
| 7.2.6.1 | Mandatory Spare of item 7.2.6 | % | 20%
Main Equipment
| 7.3 | 220kV Busbar Distributed Type Protection System, including:
| 7.3.1 | 220kV Busbar Protection Relay central module ACC. To PSLD drawing | No. | 2
| 7.3.2 | 220kV Busbar Protection Relay bay modules ACC. To PSLD drawing | No. | 4
Mandatory Spare Parts
| 7.3.3 | 220kV Busbar Protection Relay bay module ACC. To PSLD drawing | No. | 1
Main Equipment
| 7.3.4 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 2
Mandatory Spare Parts
| 7.3.4.1 | All panel accessories acc. to item 7.3.2 | % | 20%
| 7.4 | Power Transformer Automatic Voltage Regulation including:
| 7.4.1 | Automatic Voltage Regulator Relay | No. | 2
Mandatory Spare
| 7.4.1.1 | Automatic Voltage Regulator Relay | No. | 1
Main Equipment
| 7.4.2 | Panels with all accessories and auxiliaries, lighting, heating, socket, push buttons, wiring, terminals, test facilities, discrepancy and all other switches, labels, unit measurement indicating lamps, position indicators, alarm announciators, temperature indicators, test block/plug , Labels, etc. and with the following equipment. | No. | 2
Mandatory Spare Parts
| 7.4.2.1 | All panel accessories acc. to item 7.4.2 | % | 20%
Main Equipment
| 7.5 | All other equipment required for completion of the 220kV protection system which have not been mentioned in the above rows Speicificly. | Lot | 1
TOTAL PRICE ITEM 7
TOTAL PRICE ITEM 7_Spare Parts
| 8 | 400/220kV SUBSTATION AUTOMATION and CONTROL SYSTEM
Main Equipment
| 8.1 | All software and licenses | Lot | 1
| 8.2 | Bay Control Units (BCU) (with all required functions as per PSLD) | No. | 16
Mandatory Spare Parts
| 8.2.1 | Bay Control Units (BCU) (with all required functions as per PSLD) | No. | 4
Main Equipment
| 8.3 | Bay Control Panels | No. | 6
| 8.4 | Auxiliary and Common Services Bay Control Unit | Lot | 1
| 8.5 | Auxiliary and Common Services Panel including all accessories | Lot | 1
| 8.6 | PRP communication Station level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
| 8.7 | PRP communication Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
Mandatory Spare Parts
| 8.7.1 | LAN Switches (Ports, Star-Coupler, Fibre Optic Cables etc.) | % | 20%
Main Equipment
| 8.8 | Substation Computer (server) | No. | 2
| 8.9 | Operator Work Station with all required peripherals and monitor | Lot | 2
| 8.10 | Engineering Work Station with all required peripherals and monitor | No. | 1
| 8.11 | Gateway, Converter, Modem and firewall and all other required equipment. | No. | 2
| 8.12 | GPS, Tiem Server, GPS Antenna and all other required equipment. | No. | 1
| 8.13 | SOE Printer | No. | 1
| 8.14 | Station Log Printer | No. | 1
| 8.15 | General Purpose Printer | No. | 1
TOTAL PRICE ITEM 8
TOTAL PRICE ITEM 8_Spare Parts
| 9 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
Main Equipment
| 9.1 | Differential protection relays with all required accessories (to be installed instead of existing distance relays of Suswa and Isinya lines) | Sets | 2
TOTAL PRICE ITEM 9
| 10 | TELECOMMUNICATION & NCC/RCC/NSCC
Main Equipment
| 10.1 | New Telecommunication and SDH System for 400/220kV Substation including:
| 10.1.1 | Panel (800*600*2260mm) with all required accessories | No. | 1
| 10.1.2 | Basic modules are included: Backplane, Main controler, Supply board, etc. | No. | 1
| 10.1.3 | Optical Interface Board STM-16 (2*ports) | No. | 3
| 10.1.4 | SFP Moudule | No. | 6
| 10.1.5 | E1 Interface Board | No. | 2
| 10.1.6 | FE Interface Board (SCADA) | No. | 1
| 10.1.7 | FE Interface Board (Office LAN) | No. | 1
| 10.1.8 | 2- Wire telephone Interface Board | No. | 1
| 10.1.9 | RS-232 Data Board | No. | 1
| 10.1.10 | Protection Interface Board for Differential protection relay (4 ports supposed for each card) OPIC card | No. | 6
| 10.1.11 | Protection Interface Board for Distance (4 ports supposed for each card) TEPI cards | No. | 4
Mandatory Spare Parts
| 10.1.11.1 | Telecommunication system ports (4 ports supposed for each card) | No. | 1
Main Equipment
| 10.2 | New Firewall system with all necessary Licenses | Lot | 1
| 10.3 | New IP phone Equipment with licences, switches, etc. (at least 2x indoor & 2x outdoor) for Kimuka 400/220kV substation
| 10.3.1 | Phone set | No. | 4
| 10.3.2 | Telephone Junction Box | Lot | 1
| 10.3.3 | LAN Cable | Lot | 1
| 10.3.4 | Outdoor Cabin | No. | 2
Mandatory Spare Parts
| 10.3.5 | Mandatory Spare for New IP phone Equipment (Indoor/Outdoor) including: Power Supply,Patch cord,Head set,Head set cord, Wall mount kit, Expansion Moudle ... etc. | Lot | 1
Main Equipment
| 10.4 | Required equipment for modification works at existing Kimuka 220/66kV substation;
| 10.4.1 | Required equipment for modification works at existing Telecommunication and SDH System in 220/66kV Substation | Lot | 1
| 10.4.2 | Required equipment for modification works at existing Teleprotection Signalling Equipment in 220/66kV Substation | Lot | 1
| 10.5 | Required equipment for modification works at existing Suswa 400/220/132 KV substation;
| 10.5.1 | Required equipment for modification works at existing Telecommunication and SDH System in Suswa 400/220 KV substation included: | Lot | 1
| 10.5.2 | Required equipment for modification works at existing Teleprotection Signalling Equipment in existing Suswa 400/220 KV substation | Lot | 1
| 10.6 | Required equipment for modification works at existing Isinya 400 KV substation;
| 10.6.1 | Required equipment for modification works at existing Telecommunication and SDH System in existing Isinya 400 KV substation | Lot | 1
| 10.6.2 | Required equipment for modification works at existing Teleprotection Signalling Equipment in existing existing Isinya 400 KV substation | Lot | 1
| 10.7 | Required equipment for incorporating new and existing substation's signals into the SCADA/EMS System at the NCC/RCC/NSCC | Lot | 1
| 10.8 | Required equipment for modifications to NCC/RCC/NSCC mimic board (if any) | Lot | 1
| 10.9 | Required equipment fo modification works at existing PABX in Lessos RCC including all necessary Licenses, Network switches and any other facilities for communication with NCC, RCC and NSCC | Lot | 1
| 10.10 | All necessary licences, hardware, software and configuration needed for the existing network management system (NMS) to create the STM-16 link that forms part of the backbone network from Kimuka 400/220kV Substation and other Substations to the NCC/RCC/NSCC | Lot | 1
| 10.11 | Required equipment and accessories for interconnection between the OPGW and fibre optic cable in communication room & communication collocation room
| 10.11.1 | Optical Distribution panel (Main & Collocation Communication room) | Set | 2
| 10.11.2 | Optical Distribution Unit (OCDF) for 48 cores fiber ( Main Communication romm) | Set | 5
| 10.11.3 | Digital Distribution Unit (ODF) for 48 cores fiber | Set | 5
| 10.11.4 | Tail Optical Fiber | Lot | 1
| 10.11.5 | 48 Core Steel Tape Armoured Outdoor Optical Fiber GYXTW | Lot | 1
| 10.11.6 | Coaxial Cable | Lot | 1
| 10.11.7 | PVC Pipe suitable for the distance between entry gantry and communication room | Lot | 1
| 10.11.8 | Optical Cable plane | Lot | 1
| 10.11.9 | Steel Tube from junction box to entry of cable channel | Lot | 1
| 10.11.10 | OPGW Splice Closures joint box with all accessories | Set | 3
| 10.12 | EPABX system for communication between guard house and individual Staff housings including:
| 10.12.1 | Exchange | Lot | 1
| 10.12.2 | Telephone equipment | No. | 16
| 10.12.3 | Junction boxes | Lot | 1
| 10.12.4 | Cabling | Lot | 1
| 10.12.5 | Power supply with backup battery | Lot | 1
Main Equipment
TOTAL PRICE ITEM 10
TOTAL PRICE ITEM 10_Spare Parts
| 11 | LV CABLES AND ACCESSORIES
Main Equipment
| 11.1 | Auxiliary power and control cabling including single and three-phase power cables, control cables required for control, protection, metering and alarms, CTs' and CVTs' circuit cabes, DC supply cables. | Lot | 1
Mandatory Spare Parts
| 11.1.1 | All types of cables mentioned in item 11.1. | % | 10%
Main Equipment
| 11.2 | Substation internal fibre optic cabling, coaxilal cables. | Lot | 1
Mandatory Spare Parts
| 11.2.1 | All types of cables mentioned in item 11.2. | % | 10%
Main Equipment
| 11.3 | Cable laying equipment including cable trays, ladders, supports & fixing calmps, glands, lugs, terminals, rails, labels, cable shoes, accessories, fire proof sealing of ducts/conduits/openings, and etc. | Lot | 1
Mandatory Spare Parts
| 11.3.1 | Cable laying equipment acc. to item 11.3. | % | 10%
TOTAL PRICE ITEM 11
TOTAL PRICE ITEM 11_Spare Parts
| 12 | EARTHING & LIGHTNING PROTECTION
| 12.1 | Earthing system (including main earth grid, earth mat, rizer, bonding, connector, clamp, fitting, earth rod and well, inspection earth pits etc. as required) | Lot | 1
| 12.2 | Lightning protection system (including shield wire, air termination rod, down conductor, equipotential bonding, disconnecting link, etc. as required) | Lot | 1
TOTAL PRICE ITEM 12
| 13 | 11KV CABLE SYSTEM
Main Equipment
| 13.1 | 11kV cables for connection between A.TR. and Auxiliary & Earthng Transformer | Lot | 1
Mandatory Spare Parts
| 13.1.1 | 11kV cables for connection between A.TR. and Auxiliary & Earthng Transformer | Lot | 1 run (eq. to distance between A.TR. & EAT)
Main Equipment
| 13.2 | Cable laying equipment including, cable trays, ladders, supports & fixing calmps, accessories, glands, lugs, terminals, rails, labels, cable shoes, fire proof sealing of ducts/conduits/openings etc. | Lot | 1
| 13.3 | 11kV cable sealing end (CSE) for 11kV side of 200MVA Auto-Transformers and HV side of Auxiliary & Earthing Transformer | No. | 12
Mandatory Spare Parts
| 13.3.1 | 11kV cable sealing end (CSE) for 11kV side of 200MVA Auto Transformers and HV side of Auxiliary & Earthing Transformer | No. | 1
TOTAL PRICE ITEM 13
TOTAL PRICE ITEM 13_Spare Parts
| 14 | SUPPORT STRUCTURES
Main Equipment
| 14.1 | Steel supports for 400kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
| 14.2 | Steel supports for 220kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
| 14.3 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
| 14.4 | Miscellaneous structures for interconnecting 400kV and 220kV switchyards (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
| 14.5 | Structures for installing batteries (including all the required anti-acid hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
TOTAL PRICE ITEM 14
| 15 | AUXILIARY SUPPLY
Main Equipment
| 15.1 | LVAC system
| 15.1.1 | AC Main and distribution panels, AC distribution outdoor cubicles, fuse box for oil treatment socket with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 6
| 15.1.2 | Oil treatment panel and accessories (including heavy duty outlet socket, fuses, glands, etc.) | No. | 2
| 15.1.3 | AC distribution panels in BCR, with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 6
| 15.1.4 | Solar PV Modules, Charge Controllers, Hybrid Inverters and Batteries for Outdoor and Indoor lighting and associated panels/switchgears and accessories | Lot | 1
Mandatory Spare Parts
| 15.1.4 | Equipment and accessories mentioned in item 15.1.1, 15.1.2, 15.1.3, 15.1.4 | % | 20%
Main Equipment
| 15.2 | 110VDC system
| 15.2.1 | 110Vdc Main and distribution panels, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 5
| 15.2.2 | 110Vdc distribution panels in BCR, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 6
| 15.2.3 | 110Vdc battery chargers with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | Sets | 2
| 15.2.4 | 110Vdc batteries with structures/frames with all accessories (including Connection Bars, Cables, Luges, Bolts, Nuts, Washers, anti-Acid covers, Themometer, Density Meter, tools for battery filling and etc.) | Sets | 2
Mandatory Spare Parts
| 15.2.5 | Equipment, accessories and material mentioned in item 15.2.1, 15.2.2, 15.2.3, 15.2.4 | % | 20%
Main Equipment
| 15.3 | 48VDC system
| 15.3.1 | 48Vdc distribution panel, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 3
| 15.3.2 | 48Vdc battery chargers with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | Sets | 2
| 15.3.3 | 48Vdc batteries with structures/frames with all accessories (including Connection Bars, Cables, Luges, Bolts, Nuts, Washers, anti-Acid covers, Themometer, Density Meter, tools for battery filling and etc.) | Sets | 2
Mandatory Spare Parts
| 15.3.4 | Equipment, accessories and material mentioned in item 15.3.1, 15.3.2, 15.3.3 | % | 20%
Main Equipment
| 15.4 | 415V ac Uninterruptible Power Supply including isolating by-pass transformers, inverters, static switch, manual bypass switch, panels & distribution boards | Sets | 2
Mandatory Spare Parts
| 15.4.1 | Equipment and accessories mentioned in item 15.4 | % | 20%
Main Equipment
| 15.5 | Main Diesel Generator 500kVA including generator control and protection panel and all peripheral equipment, reservior(s), and accessories. | Set | 1
Mandatory Spare Parts
| 15.5.1 | Mechanical, Electrical & Control Equipment/Accessories of Diesel Generator | % | 20%
Main Equipment
| 15.6 | Diesel Generator 200kVA including generator control and protection panel and all peripheral equipment, reservior(s), and accessories for Technical and Security Staff Housing | Set | 1
Mandatory Spare Parts
| 15.6.1 | Mechanical, Electrical & Control Equipment/Accessories of Diesel Generator | % | 20%
TOTAL PRICE ITEM 15
TOTAL PRICE ITEM 15_S]pare Parts
| 16 | TARIFF METERING
Main Equipment
| 16.1 | Tariff metering system for 400kV OHL, complete with wiring, accessories and etc. including:
| 16.1.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 4
| 16.1.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 4
Mandatory Spare Parts
| 16.1.2.1 | Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
Main Equipment
| 16.2 | Tariff metering system for 220kV OHL feeders, complete with wiring, accessories etc. and including:
| 16.2.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
| 16.2.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
Mandatory Spare Parts
| 16.2.2.1 | Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 1
Main Equipment
| 16.3 | Tariff metering system for Auto-Transformer, complete with wiring, accessories etc. and including:
| 16.3.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
| 16.3.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
Mandatory Spare Parts
| 16.3.2.1 | Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 1
Main Equipment
| 16.4 | Tariff metering system for LVAC incomer panels, complete with wiring, accessories etc. and including:
| 16.4.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
Main Equipment
| 16.5 | Metering data collection and communication system, complete with fibre optic cabling, accessories, each kind of energy meters software and communication ports. All media and accessories in order to transferring energy meter measured values to remote center according to both KETRACO and KPLC required specification. | Lot | 1
Mandatory Spare Parts
| 16.5.1 | Required accessories for item 16.4 | % | 20%
Main Equipment
| 16.6 | Metering panel with all accessories and auxiliaries, lighting, heating, socket, wiring, terminals, test facilities, and all other switches, labels, test block/plug , Labels, etc. | No. | 3
Mandatory Spare Parts
| 16.6.1 | Required accessories for item 16.5 | % | 20%
Main Equipment
| 16.7 | All other related relays, racks, Voltage/Current test block, cubicles, terminals, As needed to complete the metering system. | Lot | 1
Mandatory Spare Parts
| 16.7.1 | Required accessories for item 16.6 | % | 20%
TOTAL PRICE ITEM 16
TOTAL PRICE ITEM 16_Spare Parts
| 17 | FAULT MONITORING SYSTEM & PMU
Main Equipment
| 17.1 | Fault and Event Monitoring System | Lot | 1
| 17.2 | Phasor Mesurment Unit (PMU) system with Separate GPS, Ethernet Switch, Industrial PC | Lot | 1
Mandatory Spare Parts
| 17.2.1 | Required accessories for item 17.1 and 17.2 | % | 20%
Main Equipment
| 17.3 | Data Aquisition Units | Lot | 1
| 17.4 | Master Station | No. | 1
| 17.5 | Local HMI | No. | 1
| 17.6 | Fault and Event Recorder Panel with all accessories such as wiring, Lighting, heater, socket, terminal, Indication lamp, transducer, control equipment, monitor, keyboard, mouse, case, printer, I/O card and etc.(all requirements for future extension must be considered) | Lot | 1
Mandatory Spare Parts
| 17.6.1 | Required accessories for item 17.6 | % | 20%
Main Equipment
| 17.7 | Phasor Mesurment Unit Panel with all accessories such as wiring, Lighting, heater, socket, terminal, Indication lamp, transducer, control equipment, monitor, keyboard, mouse, case, printer, I/O card and etc.(all requirements for future extension must be considered) | Lot | 1
Mandatory Spare Parts
| 17.7.1 | Required accessories for item 17.7 | % | 20%
TOTAL PRICE ITEM 17
TOTAL PRICE ITEM 17_Spare Parts
| 18 | MISCELLANEOUS
Main Equipment
| 18.1 | Bay Marshalling Kiosk | Lot | 1
| 18.2 | CCTV System with all ralated equipment for indoor and outdoor, including Cameras of suitable type and required specifications with poles, recorder, storage, monitor, switch, cabling, boxes, fixings, brackets and etc. (acc. to technical specifications in part 2-B, clause 10.5.4.10) | Lot | 1
Mandatory Spare Parts
| 18.2.1 | Required accessories for item 18.2 | % | 20%
Main Equipment
| 18.3 | Padlocks / Keys (for panels, outdoor equipments, doors, etc.) | Lot | 1
| 18.4 | Equipment/Bay labels, safety warning plates, road signages, room name plates, etc. | Lot | 1
| 18.5 | Tools and Appliances as stated in Clause 19 of Part 2-A of the Employer's Requirements | Lot | 1
| 18.6 | Tools and Equipment as stated in part 2-A, Clause 20 of the Employers Requirements (Bidder shall submit relevant itemized list with quantity, description and breackdown price) | Lot | 1
| 18.6.1 | Gas handling trolley including accessories | Lot | 1
| 18.6.2 | 400kV Portable Earth including Leads, chopsticks,cable, earting rods, connectors and clamps, etc. | Set | 2
| 18.6.3 | 220kV Portable Earth including Leads, Chopsticks, cable, earting rods, connectors and clamps, etc. | Set | 2
| 18.6.4 | Project Laptops with all required software as per Client's requirmenets in Part 2-A, clause 21 | No. | 8
| 18.6.5 | Rugged/Industrial Laptop for substation protection and control system (CRP/SAS) with all required softwareas, as per Client's requirmenets in Part 2-A, clause 21 | No. | 2
| 18.6.6 | Softwares and Licences as listed below and as per Part 2A AutoCAD for windows STAAD Pro DIgSILENT DIALux BIM software | Lot | 1
| 18.6.7 | Other Items in Part 2-A | Lot | 1
| 18.7 | Forklift for storage warehouse | No. | 1
| 18.8 | Any other item not included above but required to complete the project successfully. (Tenderer shall specify and include breakdown of price in his proposal) | Lot | 1
TOTAL PRICE ITEM 18
TOTAL PRICE ITEM 18_Spare Parts
| 19 | Site Transport as per Employer's Requirements, Part 2-A, Clause 32
Main Equipment
| 19.1 | Vehicles as per part 2-A, Clause 32
| 19.1.1 | Vehicle Type 2 as per Clause 32 of Part 2-A | No. | 6
| 19.1.2 | Vehicle Type 3 as per Part 2-A | No. | 3
TOTAL PRICE ITEM 19
TOTAL PRICE SCHEDULE 2A KIMUKA SUBSTATION Note: Contractor shall include all equipment and materials in his proposal, which are necessary to complete the works.
TOTAL PRICE SCHEDULE 2A KIMUKA SUBSTATION_Spare Parts

## Schedule 3A_SS
SCHEDULE NO. 3A
DESIGN SERVICES
FOR KIMUKA SUBSTATION
Note 1: All of the manufacturer's documentations including test reports, layout and dimensions drawings, datasheets, Catalogs, O&M instruction manuals, etc. shall be submitted to the Client.
Note 2: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Item No | Description | Unit | Estimated Quantity | Foreign Currency (FC1) = (FC2) = |  | Local Currency (KSh) = KENYAN SHILLINGS | Total Price
|  |  |  | Design Services |  | Design Services | Design Services
|  |  |  | Unit Price |  | Unit Price | (Quantity x Unit Price)
|  |  |  | FC1 | FC2 | KSh | FC1 | FC2 | KSh
1 | DESIGN SERVICES
1.1 | 400kV, 220kV and 11kV Primary Equipment Sizing/Rating Calculations and drawings (CB, DS, ES, CT, CVT, Auto. Transformer, earthing and Aux. transformer, NER, suspension/strain Insulators, etc.) | Lot | 1
1.2 | Detail design drawings of layout, site plan and sections | Lot | 1
1.3 | Substation earthing system design Calculations and drawings (including cross section of grounding conductor and rizer, step voltage, touch voltage, maximum potential rise, main grid resistance, etc. as required) | Lot | 1
1.4 | Lightning Protection Design calculation and drawings (including risk level assessment, protection zone, etc. as required) | Lot | 1
1.5 | Short Circuit Design Analysis (including grid short circuit level at the substation and inteconnection lines, etc. as required) | Lot | 1
1.6 | Surge/Lightning Arrester Design Calculations and drawings (including protection zone, protection margin, rated volatge, continous voltage, discharge class, etc. as required) | Lot | 1
1.7 | Insulation coordination studies | Lot | 1
1.8 | Buswork Electrical and mechanical Calculations and drawings (Including stranded/tubular conductors sizing, Continous and Short Circuit Current Carring Capacity, Corona Level or Surface Volatge Gradient, Electromechanical Forces due to Wieght, Ice,Wind and Short Circuit for buasbars, gantry and between equipment, post insulator, and etc. as required) | Lot | 1
1.9 | Conductors Sag and Tension Calculations and drawings | Lot | 1
1.10 | MV cables calculations and drawings | Lot | 1
1.11 | LVAC/LVDC/UPS auxiliary supply systems, EAT and Diesel Generator sets sizing, chargers, batteries design calculations and drawings | Lot | 1
1.12 | Protection, control, fault monitoring/ metering system design calculations, drawings and logic diagram together with relays' configuration, setting calculations and studies | Lot | 1
1.13 | Substation automation system (SAS) design calculations and drawings | Lot | 1
1.14 | Telecommunication system design calculations and drawings (for communication with NCC/RCC/NSCC) | Lot | 1
1.15 | Substation access control system and CCTV design calculations and drawings | Lot | 1
1.16 | External and internal lighting design calculations and drawings | Lot | 1
1.17 | LV cables and cable laying design calculations and drawings | Lot | 1
1.18 | Gantry and steel structures calculations and drawings | Lot | 1
1.19 | Equipment foundations calculations and drawings | Lot | 1
1.20 | Main and Aux. Transformers foundations, plinth, firewall, oil pits, and etc., calculations and drawings | Lot | 1
1.21 | Cable trenches/ ducts calculations and drawings | Lot | 1
1.22 | Control building, BCRs, technical/security staff housings, guard house and Telecom collocation room, diesel generator house, storage warehouse, fire water pump house design calculations and drawings | Lot | 1
1.23 | All relevant substation civil works design calculations and drawings to ensure a fully functional substation including borehole, plumbing, landscaping, parking, fence, entrance gate, etc. | Lot | 1
1.24 | Substation access road (tarmac) design calculations and drawings | Lot | 1
1.25 | Substation external access road design calculations and drawings | Lot | 1
1.26 | HVAC air-conditioning design calculations and drawings | Lot | 1
1.27 | Drainage, sewage and plumbing works design calculations and drawings | Lot | 1
1.28 | Steel water tanks support structures | Lot | 1
1.29 | Water Solar Heating System design calculations and drawings | Lot | 1
1.30 | Firefighting system, Transformer fire protection system design calculations and drawings | Lot | 1
1.31 | Other required detail design drawings | Lot | 1
1.32 | Design review meeting as specified in the Employer's Requirements Part 2-A Clause 31.3 | Lot | 1
1.33 | Preparation of Approved As-Built drawings of Kimuka 400/220kV SS | Lot | 1
1.34 | Revise of all relevant As-Built drawings of existing 220/66kV Kimuka substation, Isinya 400/220kV substation & Suswa 400/220kV substation & etc. | Lot | 1
1.35 | TOTAL PRICE SCHEDULE 3A KIMUKA SUBSTATION Note: Contractor shall include all design services in his proposal, which are necessary to complete the works.
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In practice the listed items are not be part of design. This issue needs to be discussed and revised Reply: This comment is not clear. The listed items are part of design its just the consultant decided to break them down than is normally the case and this is probably for ease of payment of design progress. Can be discussed further.

## Schedule 4A_SS
SCHEDULE NO. 4A
INSTALLATION AND OTHER SERVICES
FOR KIMUKA SUBSTATION
Note: All of the blank cells shall be filled with quoted price or "included". Any other alternation interpreted as "included". It means that relevant price has been included in other items.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Item No | Description | Unit | Estimated Quantity | Foreign Currency (FC1) = Foreign Currency (FC2) = Local Currency (KSh) = KENYAN SHILLINGS |  |  | Total Price
|  |  |  | Installation and other Services |  |  | Installation and other Services
|  |  |  | Unit Price |  |  | (Quantity x Unit Price)
|  |  |  | FC1 | FC2 | KSh | FC1 | FC2 | KSh
1 | 400kV PRIMARY PLANT
1.1 | Circuit Breaker single pole operated, 3 phase | No. | 10
1.2 | Motorized Disconnector (3-phase), complete with one integral motorised earth switch, and earth mat | No. | 20
1.3 | Motorized Disconnector (3-phase), complete with two integral motorised earth switches and earth mat | No. | 6
1.4 | Motorized Earthing switch (3-phase), with earth mat | No. | 2
1.5 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 18
1.6 | Post insulator | Lot | 1
1.7 | Insulator string (Suspension and Strain types with harware fitting) | Lot | 1
1.8 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) | No. | 30
1.9 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 12
1.10 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) | No. | 12
1.11 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) | No. | 12
1.12 | Capacitive voltage transformer (High Accuracy) for Tariff Metering, Two Cores (1-phase) | No. | 12
1.13 | Tubular Conductor | Lot | 1
1.14 | Stranded Conductor | Lot | 1
1.15 | Connectors and Clamps for Tubular Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
1.16 | Connectors and Clamps for Stranded Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
1.17 | Online monitoring system for 400kV Circuit Breaker | No. | 10
Remote End Substation_ISINYA
1.18 | All required primary modification works in ISINYA SS regarding to relocation of the existing 400kV SUSWA-1 OHL currently operated at 220 kV, connected to the 220 kV yard of ISINYA, to the 400 kV yard of ISINYA and Connecting to 400kV switchyard, which includes completion of the connection between feeder’s equipment (LA-CVT-CVT-CT) and connection of the LA to the 400kV SUSWA-1 OHL as per scope of work. This also includes Feeder name label changes in the switchyard. | Lot | 1
Remote End Substation_SUSWA
1.19 | All required primary modification works in Suswa SS regarding to Relocation of the existing 400kV ISINYA-1 OHL currently operated at 220 kV, connected to the 220 kV yard of Suswa, to the 400 kV switchyard of Suswa as per scope of work. This also includes Feeder name label changes in the switchyard. | Lot | 1
1.18 | TOTAL PRICE ITEM 1
2 | 220kV PRIMARY PLANT
2.1 | Circuit breaker single pole operated, 3 phase | No. | 6
2.2 | Motorized Disconnector (3-phase), complete with one integral motorised earth switch, and earth mat | No. | 12
2.3 | Motorized Disconnector (3-phase), complete with two integral motorised earth switches and earth mat | No. | 4
2.4 | Motorized Earthing switch (3-phase), with earth mat | No. | 2
2.5 | Surge arrester (1-phase) including surge counter and earth leakage meter | No. | 12
2.6 | Post insulator | Lot | 1
2.7 | Insulator string (Suspension and Strain types with harware fitting) | Lot | 1
2.8 | Post type current transformer for Protection and Measuring, Five Cores (1-phase) | No. | 18
2.9 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 6
2.10 | Post type current transformer (High Accuracy) for Tariff Metering, Two Cores, (1-phase) | No. | 6
2.11 | Capacitive voltage transformer, for Protection and Measuring, Two Cores (1-phase) | No. | 12
2.12 | Capacitive voltage transformer, for Protection and Measuring, Three Cores (1-phase) | No. | 6
2.13 | Capacitive voltage transformer (High Accuracy) for Tariff Metering , Two Cores (1-phase) | No. | 6
2.14 | Tubular Conductor | Lot | 1
2.15 | Stranded Conductor | Lot | 1
2.16 | Connectors and Clamps for Tubular Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
2.17 | Connectors and Clamps for Stranded Conductors (together with stainless steel nuts, bolts, bimetal) | Lot | 1
Remote End Substation_ISINYA
2.18 | All required primary modification works in ISINYA SS regarding to removal of the existing connection of 220kV OHL which already connected to diameter no.2 as per scope of work. This also includes Feeder name label changes in the switchyard. | Lot | 1
2.19 | All required primary modification works in ISINYA SS regarding to connections of the secondary side of the 400/220kV IBT-1 to 220kV Switchyard which is including the recovery of the existing LA and installation of new LA to transformer side and installation of new PI , and completing the connection of feeder’s equipment such as CSE to PI and LA to 220kV bushings as per scope of work. This also includes Feeder name label changes in the switchyard. | Lot | 1
Remote End Substation_SUSWA
2.20 | All required primary modification works in SUSWA SS regarding to removal of the existing connection of 220kV OHL for ISINYA-1 | Lot | 1
2.18 | TOTAL PRICE ITEM 2
3 | AUTO TRANSFORMER (A.TR.)
3.1 | Auto transformer (3-phase units) with tertiary winding HV400/LV220/TV11kV, 200MVA including HV/LV/TV/NV Bushing CT's, OLTC, RTCC,OLCM, Control Cabinet and all accessories as required acc. to Tech. Spec. and TDS | No. | 2
3.2 | Fire Protection Standard Nitrogen Injection and Oil Evacuation System (NIFPS) with all required accessories and instruments | No. | 2
3.3 | Online Condition Monitoring System with all required accessories and instruments | No. | 2
3.4 | Surge arrester (1-phase), installed in the Auto TR. 11kV cable box | No. | 6
3.5 | TOTAL PRICE ITEM 3
4 | EARTHING & AUXILIARY TRANSFORMER
4.1 | Earthing & Auxiliary transformer (3-phase units) HV11/LV0.415kV, 500KVA including HV/LV Bushing CT's and all accessories as required | No. | 2
4.2 | 50 kg wheeled Dry-Powder Fire extinguisher for Auxiliary transformer | No. | 2
4.3 | TOTAL PRICE ITEM 4
Main Equipment
5 | NEUTRAL EARTHING RESISTOR
5.1 | Neutral Earthing Resistor with associated CTs (acc. To SLD) | No. | 2
5.2 | TOTAL PRICE ITEM 5
6 | 400kV PROTECTION SYSTEMS
6.1 | 400kV OHL Protection System including:
6.1.1 | Main1 21L Protection Relay (with all required functions as per PSLD) | No. | 4
6.1.2 | Main2 87L Protection Relay (with all required functions as per PSLD) | No. | 4
6.1.3 | Auto-Reclose Relay (with all required functions and Voltage Selection Logic as per PSLD) | No. | 4
6.1.4 | Point On Wave (POW) Switching relay (Synchronous Switching Controller) (with required Voltage Selection Logic As per PLSD) | No. | 10
6.1.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
6.1.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 8
6.1.7 | All required equipment for modification works in remote Existing Isinya and Suswa substations, differential relays settings and etc. | Lot | 1
6.2 | 400kV HV Transformer Protection System including:
6.2.1 | Main 87T+87N Protection (with all required functions as per PSLD) | No. | 2
6.2.2 | Backup 50/51(N) Protection (with all required functions as per PSLD) | No. | 2
6.2.3 | 87HVC Connection Protection (with all required functions as per PSLD) | No. | 2
6.2.4 | Earth Fualt 50N/51N (SBEF) Protection (with all required functions as per PSLD) | No. | 2
6.2.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
6.2.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 4
6.3 | 400kV Distributed type Busbar Protection System, including:
6.3.1 | Busbar Protection Relays with bay module and central module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) | No. | 2
6.3.2 | Busbar Protection Relay bay module ACC. To PSLD drawing and considering future extention(with all required functions as per PSLD) | No. | 8
6.3.3 | Panels including all accessories, e.g. trip circuit supervision, trip relays, aux. relays, test and terminal blocks, timers, wiring etc. to make the system complete | No. | 2
6.4 | All other required works for completion of the 400kV protection system which have not been mentioned in the above rows Speicificly. | Lot | 1
6.5 | TOTAL PRICE ITEM 6
7 | 220KV PROTECTION SYSTEMS
7.1 | 220kV OHL Protection System including:
7.1.1 | Main1 87L Protection (with all required functions as per PSLD) | No. | 2
7.1.2 | Main 2 87L Protection (with all required functions as per PSLD) | No. | 2
7.1.3 | Auto-Reclose Relay (with all required functions and Voltage Selection Logic as per PSLD) | No. | 2
7.1.4 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; end fault; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
7.1.5 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 4
7.1.6 | Modification works in remote Existing Kimuka substation, differential relays settings and etc. | Lot | 1
7.2 | 220kV LV Transformer Protection System including:
7.2.1 | Backup 67/67(N) Protection(with all required functions as per PSLD) | No. | 2
7.2.2 | 87LVC Connection Protection (with all required functions as per PSLD) | No. | 2
7.2.3 | Tertiary Winding 50TV/51TV (N) Overcurrent Protection(with all required functions as per PSLD) | No. | 2
7.2.4 | Earthing Transformer 87NTV 11kV side (with all required functions as per PSLD) | No. | 2
7.2.5 | All other relays or functions such as over voltage; under voltage; trip; tripcircuit supervison; pole discordance; synchro check; fuse failure; close; lockout; short zone; circuit breaker failure, cubicles, test blocks/plugs, aux. relays, timers, terminals, Labels, etc. as needed to complete the protection. | Lot | 1
7.2.6 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 4
7.3 | 220kV Busbar Distributed Type Protection System, including:
7.3.1 | 220kV Busbar Protection Relays Distributed Type with bay modules and central modules ACC. To PSLD drawing | No. | 2
7.3.2 | 220kV Busbar Protection Relay bay modules ACC. To PSLD drawing | No. | 4
7.3.3 | Panels including all accessories, e.g. trip circuit supervision, trip relays, test terminal blocks, wiring etc. to make the system complete | No. | 2
7.4 | Power Transformer Automatic Voltage Regulation including:
7.4.1 | Automatic Voltage Regulator Relay | No. | 2
7.4.2 | Panels with all accessories and auxiliaries, lighting, heating, socket, push buttons, wiring, terminals, test facilities, discrepancy and all other switches, labels, unit measurement indicating lamps, position indicators, alarm announciators, temperature indicators, test block/plug , Labels, etc. and with the following equipment. | No. | 2
7.5 | All other required works for completion of the 220kV protection system which have not been mentioned in the above rows Speicificly. | Lot | 1
7.6 | TOTAL PRICE ITEM 7
8 | 400/220kV SUBSTATION AUTOMATION and CONTROL SYSTEM
8.1 | All software and licenses | Lot | 1
8.2 | Bay Control Units (BCU) (with all required functions as per PSLD) | No. | 16
8.3 | Bay Control Panels | No. | 6
8.4 | Auxiliary and Common Services Bay Control Unit | Lot | 1
8.5 | Auxiliary and Common Services Panel including all accessories | Lot | 1
8.6 | PRP communication Station level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
8.7 | PRP communication Bay level LAN (Switches, Star-Coupler, Fibre Optic Cables etc.) | Lot | 1
8.8 | Substation Computer (server) | No. | 2
8.9 | Operator work station | No. | 2
8.10 | Engineering Workstation | No. | 1
8.11 | Gateway, Converter, Modem and firewall and all other required equipment. | No. | 2
8.12 | GPS, Tiem Server, GPS Antenna and all other required equipment. | No. | 1
8.13 | SOE Printer | No. | 1
8.14 | Station Log Printer | No. | 1
8.15 | General Purpose Printer | No. | 1
8.16 | Modification works in Existing Kimuka substation including SCADA /SAS feeder naming change in SLD and in alarm/events, Relay/BCU Feeder name change, Panel Label changes etc | Lot | 1
8.17 | Modification works in Existing Suswa substation including SCADA /SAS feeder naming change in SLD and in alarm/events, Relay/BCU Feeder name change, Panel Label changes etc | Lot | 1
8.18 | Modification works in Existing Isinya substation including SCADA /SAS feeder naming change in SLD and in alarm/events, Relay/BCU Feeder name change, Panel Label changes etc | Lot | 1
8.19 | TOTAL PRICE ITEM 8
9 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
9.1 | All required modification works at Isinya SS including re-setting, re-testing and re-commissioning. This also includes disconnection and handover of the existing line protection panel; installation, testing and commissioning of the existing IBT-1 220 kV relay panel | Lot | 1
9.2 | All required modification works at Suswa SS including re-setting, re-testing and re-commissioning | Lot | 1
9.3 | All required modification works at Kimuka SS including re-setting, re-testing and re-commissioning. This also includes dismantling and handover of the existing distance protection relays for Isinya and Suswa circuits; installation, retrofitting, re-setting, re-testing and re-commissioning of the new differential relays as well as the existing relays | Lot | 1
9.5 | TOTAL PRICE ITEM 9
10 | TELECOMMUNICATION & NCC/RCC/NSCC
10.1 | New Telecommunication and SDH System for 400/220kV Substation including:
10.1.1 | Panel (800*600*2260mm) with all required accessories | No. | 1
10.1.2 | Basic modules are included: Backplane, Main controler, Supply board, etc. | Lot | 1
10.1.3 | Optical Interface Board STM-16 | No. | 3
10.1.4 | SFP Moudule | No. | 6
10.1.5 | E1 Interface Board | No. | 2
10.1.6 | FE Interface Board (SCADA) | No. | 2
10.1.7 | FE Interface Board (Office LAN) | Lot | 1
10.1.8 | 2- Wire telephone Interface Board | Lot | 1
10.1.9 | RS-232 Data Board | Lot | 1
10.1.10 | Protection Interface Board for Differential protection relay (4 ports supposed for each card) OPIC card | No. | 6
10.1.11 | Protection Interface Board for Distance (4 ports supposed for each card) TEPI cards | No. | 4
10.2 | New IP phone Equipment with licences, switches, etc. (at least 2x indoor & 2x outdoor) for Kimuka 400/220kV substation
10.2.1 | Phone set | No. | 4
10.2.2 | Telephone Junction Box | Lot | 1
10.2.3 | LAN Cable | Lot | 1
10.2.4 | Outdoor Cabin | No. | 2
10.3 | Modification works at existing Kimuka 220/66kV substation;
10.3.1 | Modification works at existing Telecommunication and SDH System in 220/66kV Substation | Lot | 1
10.3.2 | Modification works at existing Teleprotection Signalling Equipment in 220/66kV Substation | Lot | 1
10.4 | Modification works at existing Suswa 400/220/132 KV substation;
10.4.1 | Modification works at existing Telecommunication and SDH System in Suswa 400/220 KV substation included: | Lot | 1
10.4.2 | Modification works at existing Teleprotection Signalling Equipment in existing Suswa 400/220 KV substation | Lot | 1
10.5 | Modification works at existing Isinya 400 KV substation;
10.5.1 | Modification works at existing Telecommunication and SDH System in existing Isinya 400 KV substation | Lot | 1
10.5.2 | Modification works at existing Teleprotection Signalling Equipment in existing existing Isinya 400 KV substation | Lot | 1
10.6 | Required works for incorporating new and existing substation's signals into the SCADA/EMS System at the NCC/RCC/NSCC | Lot | 1
10.7 | Modifications to NCC/RCC/NSCC databases and applications including feeder name changes in alarm/events for the existing stations | Lot | 1
10.8 | Update of the Geographic Map | Lot | 1
10.9 | Modifications to NCC/RCC/NSCC operator displays including feeder name changes for the existing stations | Lot | 1
10.10 | Required modifications to NCC/RCC/NSCC mimic board (if any) | Lot | 1
10.11 | Modification works at existing PABX in Lessos RCC including all necessary Licenses, Network switches and any other facilities for communication with NCC, RCC and NSCC | Lot | 1
10.12 | All necessary licences, hardware, software and configuration needed for the existing network management system (NMS) to create the STM-16 link that forms part of the backbone network from Kimuka 400/220kV Substation and other Substations to the NCC/RCC/NSCC | Lot | 1
10.13 | Required works for interconnection between the OPGW and fibre optic cable (including joint box, etc.)
10.11.1 | Optical Distribution panel (Main & Collocation Communication room) | Set | 2
10.11.2 | Optical Distribution Unit (OCDF) for 48 cores fiber ( Main Communication romm) | Set | 5
10.11.3 | Digital Distribution Unit (ODF) for 48 cores fiber | Set | 5
10.11.4 | Tail Optical Fiber | Lot | 1
10.11.5 | 48 Core Steel Tape Armoured Outdoor Optical Fiber GYXTW | Lot | 1
10.11.6 | Coaxial Cable | Lot | 1
10.11.7 | PVC Pipe suitable for the distance between entry gantry and communication room | Lot | 1
10.11.8 | Optical Cable plane | Lot | 1
10.11.9 | Steel Tube from junction box to entry of cable channel | Lot | 1
10.11.10 | OPGW Splice Closures joint box with all accessories | Set | 3
10.12 | EPABX system for communication between guard house and individual Staff housings including:
10.12.1 | Exchange | Lot | 1
10.12.2 | Telephone equipment | No. | 16
10.12.3 | Junction boxes | Lot | 1
10.12.4 | Cabling | Lot | 1
10.12.5 | Power supply with backup battery | Lot | 1
10.13 | New Firewall system with all necessary Licenses | Lot | 1
10.16 | TOTAL PRICE ITEM 10
11 | LV CABLES AND ACCESSORIES
11.1 | Auxiliary power and control cabling including single and three-phase power cables, control cables required for control, protection, metering and alarms, CTs' and CVTs' circuit cabes, DC supply cables. | Lot | 1
11.2 | Substation internal fibre optic cabling, coaxilal cables. | Lot | 1
11.3 | Cable laying equipment including cable trays, ladders, supports & fixing calmps, glands, lugs, terminals, rails, labels, cable shoes, accessories, fire proof sealing of ducts/conduits/openings, and etc. | Lot | 1
11.4 | TOTAL PRICE ITEM 11
12 | EARTHING & LIGHTNING PROTECTION
12.1 | Earthing system (including main earth grid, earth mat, rizer, bonding, connector, clamp, fitting, earth rod and well, inspection earth pits etc. as required) | Lot | 1
12.2 | Lightning protection system (including shield wire, air termination rod, down conductor, equipotential bonding, disconnecting link, etc. as required) | Lot | 1
12.3 | TOTAL PRICE ITEM 12
13 | 11KV CABLE SYSTEM
13.1 | 11kV cables for connection between A.TR. and Auxiliary & Earthng Transformer | Lot | 1
13.2 | Cable laying equipment including, cable trays, ladders, supports & fixing calmps, accessories, glands, lugs, terminals, rails, labels, cable shoes, fire proof sealing of ducts/conduits/openings etc. | Lot | 1
13.3 | 11kV cable sealing end (CSE) for 11kV side of 200MVA Auto-Transformers and HV side of Auxiliary & Earthing Transformer | No. | 12
13.4 | TOTAL PRICE ITEM 13
14 | SUPPORT STRUCTURES
14.1 | Steel supports for 400kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
14.2 | Steel supports for 220kV equipment and accessories (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
14.3 | Gantries and other structures within the Substation (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
14.4 | Miscellaneous structures for interconnecting 400kV and 220kV switchyards (including all the required hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
14.5 | Structures for installing batteries (including all the required anti-acid hot dip galvanised steel, bolts, nuts, anchore bolts, plates and etc.) | Lot | 1
14.5 | TOTAL PRICE ITEM 14
15 | CIVIL WORKS Note: All required material and works shall be included in the quoted price in this section.
15.1 | Site survey | Lot | 1
15.2 | Site clearance including removal of shrubs, bushes, vegetation, buildings, foundations as necessary | Lot | 1
15.3 | Earth works including excavation, backfilling and excavation in rock up to a depth of 2m | Lot | 1
15.4 | Soil Investigation (Geotechnical and geo-electrical) (Boreholes and trial pits) | Lot | 1
15.5 | Temporary works | Lot | 1
15.6 | Grading and landscaping on completion | Lot | 1
15.7 | Surfacing with gravel | Lot | 1
15.8 | Drainage system including Excavation, Backfill, Channel Slopping, Lean Conceret, Reinforcement, Formwork, Concrete Placement, Concrete Curing, Grating Plates, Filter aggregates, etc. | Lot | 1
15.9 | Sewage system (including Polyethylene Pipes, PVC Vent Pipes, Toilet, Septic Tanks with sufficient size, Floor drain, Valves, etc.)
15.9.1 | Underground Polyethylene Septic Tank for control building and Guard house, 6m^3 | No. | 1
15.9.2 | Underground Polyethylene Septic Tank for Technical staff Housing and Security staff Housing, 6m^3 | No. | 1
15.9.3 | Polyethylene Pipes, PVC Vent Pipes, Toilet, Floor drain, Valves, etc. | No. | 1
15.10 | Complete water supply system (potable water and fire water) including borehole, 30,000-liter and 5000-liter reservoirs pumps, pipes, valves, control panel, electric motors, indicative gauges/meters, etc.
15.10.1 | Water Pump for Control building and Guard house, 6 m^3/hr | No. | 2
15.10.2 | Water Pump for Technical staff Housings and Security staff Housings, 6 m^3/hr | No. | 2
15.10.3 | Main water supply prestressed steel water tank (30,000 lit.) with automatic control | No. | 1
15.10.4 | Elevated prestressed water supply tank (5000 liters X 4) with automatic control for control building, guard house, staff housings, etc. | No. | 5
15.10.5 | Water system plumbing and accessories to circulate water from borehole to 30,000-liter reservoir and 5000-liter elevated water tanks (adjacent to manned buildings) | Lot | 1
15.10.6 | Borehole and all associated piping systems and pumps | Lot | 1
15.11 | Substation land boundary chain-link fence including security for watch and ward during construction phase, as per bid drawings | Lot | 1
15.12 | Switchyard chain-link fence as required | Lot | 1
15.13 | Substation gates and access control system | Lot | 1
15.14 | Cable trenches / ducts including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. | Lot | 1
15.15 | Substation road and fence Lighting System, with all ralated equipment including Lighting fixture and terminal boxes, Steel lighting poles with related terminals, fuses, fixtures, lamps and etc., cables and related accessories, distribution boards and etc. | Lot | 1
15.16 | Substation Control Building Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, HVAC, Water Solar Heating, Fire Detection and fire extinguishers (handheld and trolley-mounted), fire blankets, access control, etc.
15.16.1 | Construction of Substation Control Building (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, access control, etc. (Acc. to bid drawings) | m^2 | 675
15.16.2 | Complete Split Unit, 9000 BTU/hr for Communication Room, Meeting Room, Office, Operator & Scada Room | No. | 4
15.16.3 | Complete Split Unit, 12000 BTU/hr for AC/DC Room | No. | 2
15.16.4 | Complete Split Unit-24000 BTU/hr for Relay Room | Lot | 1
15.16.5 | Exhaust Fan, 270 m3/hr for Toilets | No. | 2
15.16.6 | Hood-450 CFM for Kitchen | No. | 1
15.16.7 | Exhaust Fan, 2900 m3/hr for Battery Room (suitable for hazardous area) | No. | 2
15.16.8 | Dry-Powder Fire extinguishers, 12 Kg for Store, AC/DC room, Archive Room, Communication Room, Meeting Room, Office, Operator & Scada Room, Relay Room, and Corridor (as required acc. to bid documents) | No. | 9
15.16.9 | CO2 Fire extinguishers, 6 Kg for Store, AC/DC room, Archive Room, Communication Room, Meeting Room, Office, Operator & Scada Room, Relay Room, and Corridor (as required acc. to bid documents) | No. | 9
15.16.10 | Solar Water Heater with backup electric heating element | Lot | 1
15.16.11 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
15.17 | Substation Guard House and Telecom Collocation Room Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services e.g. Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, HVAC (DX split units, fans, etc.), Water Solar Heating, Fire Detection and portable fire extinguishers (handheld and trolley-mounted), fire blankets, access control, etc.
15.17.1 | Construction of Substation Guard House and Telecom Collocation Room (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, access control, etc. (Acc. to bid drawings) | m^2 | 93
15.17.1 | Complete Split Unit, 9000 BTU/hr for Customer Room, Main Equipment Room, Office, and Guard Room | No. | 4
15.17.2 | Exhaust Fan, 270 m3/hr for Toilets | No. | 2
15.17.3 | Exhaust Fan, 240 m3/hr for Battery Room (suitable for hazardous area) | No. | 1
15.17.4 | Hood-450 CFM for Kitchen | No. | 1
15.17.5 | Dry-Powder Fire extinguishers, 12 Kg for Customer Room, Main Equipment Room, Office, Guard Room, and Battery Room (as required acc. to bid documents) | No. | 5
15.17.6 | CO2 Fire extinguishers, 6 Kg for for Customer Room, Main Equipment Room, Office, Guard Room, and Battery Room (as required acc. to bid documents) | No. | 5
15.17.7 | Solar Water Heater with backup electric heating element | Lot | 1
15.17.8 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
15.18 | Fire Detection and Alarm System (for Buildings) | Lot | 1
15.19 | Covered Car parking including foundation and structure equipped with sunshade suitable for 10 cars (acc. to bid drawings) | m^2 | 140
15.20 | Foundation of 400kV equipment/support structures, including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. (Acc. to Bid Drawings/Documents) | Lot | 1
15.21 | Foundation of 220kV equipment/support structures, including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. (Acc. to Bid Drawings/Documents) | Lot | 1
15.22 | Foundation of gantries and other structures within substation (Acc. to Bid Drawings/Documents) | Lot | 1
15.23 | A.TR. foundation, Plinth and oil drain pits, including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. (Acc. to Bid Drawings/Documents) | Set | 2
15.24 | Auxiliary Transformer foundation, Plinth and oil drain pit, including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. (Acc. to Bid Drawings/Documents) | Set | 2
15.25 | Miscellaneous foundation to complete the works, including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. (such as NER, DG, tanks, etc.) | Lot | 1
15.26 | Firewalls for Power Transformers and VSRs, including Excavation, Backfill, Reinforced concrete, Lean Conceret, Formatting, Grout, Reinforcement, Galvanized anchor bolt, etc. (Acc. to Bid Drawings/Documents) | Lot | 1
15.27 | Storage Warehouse including building services (e.g. Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), HVAC (fans, heaters, etc.), Fire Detection, hand held and trolley-mounted fire extinguishers and etc.)
15.27.1 | Construction of Storage Warehouse (including Excavation, concrete works, backfilling, and etc.) together with building services such as Lighting, Small Power System (including Lighting Panels, Conduits, Lighting Fixtures and etc.), Water Supply and Sewage System, access control, etc. | m^2 | 1600
15.27.2 | Wind-driven Cyclone Ventilator for Storage Warehouse, one per slope per span | No. | 20
15.27.3 | Dry-Powder Fire extinguishers, 12 Kg for Storage (as required acc. to bid documents) | No. | 4
15.27.4 | CO2 Fire extinguishers, 6 Kg for Storage (as required acc. to bid documents) | No. | 4
15.27.5 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
15.28 | Diesel generator house Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services (e.g. Lighting, Small Power System, Fire Detection and hand-held fire extinguishers)
15.28.1 | Construction of Diesel generator house (including Excavation, concrete works, backfilling, and etc.) and Building services (e.g. Lighting, Small Power System, HVAC (fans, etc.), Fire Detection hand held and trolley-mounted fire extinguishers and etc.) Acc. to bid drawings Note: As per contractor's detail design and proposed package, the building size shall be considered accordingly without any surcharge. | m^2 | 40
15.29 | Fire water pump house Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services (e.g. Lighting, Small Power System, HVAC (fans, etc.), Fire Detection hand held and trolley-mounted fire extinguishers and etc.) and borehole with underground reservoir (with adequate capacity to Client/Consultant Approval) of adequate capacity with automatic level control to serve requirements of substation yard and buildings, yard hydrant system, NFPA-listed and jockey pumps, and other required equipment/works to make a complete and functional system
15.29.1 | Construction of Fire water pump house (including Excavation, concrete works, backfilling, and etc.) and Building services (e.g. Lighting, Small Power System, HVAC (fans, etc.), Fire Detection hand held and trolley-mounted fire extinguishers and etc.) Acc. to bid drawings Note: As per contractor's detail design and proposed package, the building size shall be considered accordingly without any surcharge. | m^2 | 39.96
15.29.2 | Fire water supply reservoir (2 reservoirs, with total capacity of 230 m3) with automatic level control | Lot | 1
15.29.3 | Hydrant system for switchyard and at the entry of the control building. | Set | 1
15.29.4 | Fire pump package (NFPA-listed and jockey pumps, etc.) | Set | 1
15.29.5 | Other required equipment/works to make a complete and functional firefighting system | Lot | 1
15.29.6 | Dry-Powder Fire extinguishers, 12 Kg for Fire pump house (as required acc. to bid documents) | No. | 1
15.29.7 | CO2 Fire extinguishers, 6 Kg for Fire pump house (as required acc. to bid documents) | No. | 1
15.30 | Substation internal access road to bituminous standards complete with drainage facilities and culverts as necessary suitable for heavy machine's traffic, including Road leveling, Lean Conceret, Prefabricated concrete kerb, Base and Sub-base, Asphalt width 8&6&4&3 meters, etc., as per bid drawing | Lot | 1
15.31 | Substation external access road to bituminous standards from the nearest major road via a standard road junction to substation gate with channels and kerbs for drainage, with storm water draining into IBDs on either sides of the road (including Road leveling, Lean Conceret, Prefabricated concrete kerb, Base and Sub-base, Asphalt width 3.5 meters, Shoulders' width 1 meter, etc.), as per bid drawing suitable for heavy machine's traffic. Note: The access road length shall be included in the quoted price as required, and no surcharge is accepted. | km | 1
15.32 | 400 kV Bay Control Rooms (BCRs) (including Excavation, concrete works, backfilling, and etc.) together with building services (e.g. Lighting, Small Power System including Lighting Panels, Conduits, Lighting Fixtures and etc.,AC and DC panel, HVAC, Fire Detection, hand held fire extinguishers and etc.)
15.32.1 | Construction of 400 kV Bay Control Rooms (BCRs) (including Excavation, concrete works, backfilling, and etc.) and Building services (e.g. Lighting, Small Power System, Fire Detection and hand-held fire extinguishers) acc. to bid drawings | m^2 | 180
15.32.3 | Split Unit, 12000 BTU/hr for BCR | No. | 8
15.32.4 | Dry-Powder Fire extinguishers, 12 Kg for BCR | No. | 8
15.32.5 | CO2 Fire extinguishers, 6 Kg for BCR | No. | 8
15.33 | 220 kV Bay Control Rooms (BCRs) (including Excavation, concrete works, backfilling, and etc.) together with building services (e.g. Lighting, Small Power System including Lighting Panels, Conduits, Lighting Fixtures and etc., ,AC and DC panel, HVAC, Fire Detection, hand held fire extinguishers and etc.)
15.33.1 | Construction of 220 kV Bay Control Rooms (BCRs) (including Excavation, concrete works, backfilling, and etc.) and Building services (e.g. Lighting, Small Power System, Fire Detection and hand-held fire extinguishers) acc. to bid drawings | m^2 | 90
15.33.3 | Split Unit, 12000 BTU/hr for BCR | NO. | 4
15.33.4 | Dry-Powder Fire extinguishers, 12 Kg for BCR | No. | 4
15.33.5 | CO2 Fire extinguishers, 6 Kg for BCR | No. | 4
15.33.6 | MISCELLANEOUS PRICES FOR FOUNDATION WORKS: Special foundation works including pile caps, beams and modification to normal foundation to adapt specified foundation conditions to cater for particular soil conditions. NB: These shall only be applicable stated works have been approved by the Employer/Employer's Representative and executed
15.33.6 | Stone masonry retaining wall in cement:sand (1:3) mortar | Square meter | 100
15.33.6 | 1m x 1m x 1m rock filled gabion installed to protect foundations against erosion | Linear Meter | 500
15.33.6 | Additional structural concrete (grade C25/30 per eurocode notation) including cost of formwork | cubic meter | 300
15.33.6 | Additional excavation including reinstatement | cubic meter | 600
15.33.6 | Additional steel reinfocing bars including supply, bending and placing | tonnes | 10
15.33.6 | Solid rock excavation (including reinstatement) | cubic meter | 10000
15.33.6 | Rip-rap stone work, 0.5m deep to protect against erosion | Square meter | 1000
15.33.6 | Imported Backfill material including placement | cubic meter | 10000
15.34 | TOTAL PRICE ITEMS 15
16 | AUXILIARY SUPPLY
16.1 | LVAC system
16.1.1 | AC Main and distribution panels, AC distribution outdoor cubicles with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 6
16.1.2 | Oil treatment panel and accessories (including heavy duty outlet socket, fuse box, fuses, glands, etc.) | No. | 2
16.1.3 | AC distribution panels in BCR, with all required equipment and accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 6
16.1.4 | Solar PV Modules, Charge Controllers, Hybrid Inverters and Batteries for Outdoor and Indoor lighting and associated panels/switchgears and accessories | Lot | 1
16.2 | 110VDC system
16.2.1 | 110Vdc Main and distribution panels, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 5
16.2.2 | 110Vdc distribution panels in BCR, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 6
16.2.3 | 110Vdc battery chargers with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | Sets | 2
16.2.4 | 110Vdc batteries with structures/frames with all accessories (including Connection Bars, Cables, Luges, Bolts, Nuts, Washers, anti-Acid covers, Themometer, Density Meter, tools for battery filling and etc.) | Sets | 2
16.3 | 48VDC system
16.3.1 | 48Vdc distribution panel, fuse boxes, with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | No. | 3
16.3.2 | 48Vdc battery chargers with all required accessories (including CBs, Contactors, Metering and Protection, Fuses, Aux. Relays and etc.) | Sets | 2
16.3.3 | 48Vdc batteries with structures/frames with all accessories (including Connection Bars, Cables, Luges, Bolts, Nuts, Washers, anti-Acid covers, Themometer, Density Meter, tools for battery filling and etc.) | Sets | 2
16.4 | 415V ac Uninterruptible Power Supply Panel including isolating by-pass transformers, inverters, static switch, manual bypass switch, panels & distribution boards | No. | 2
16.5 | Main Diesel Generator 500kVA including generator control and protection panel and all peripheral equipment, reservior(s), and accessories. | Set | 1
16.6 | TOTAL PRICE ITEM 16
17 | TARIFF METERING
17.1 | Tariff metering system for 400kV OHL, complete with wiring, accessories and etc. including:
17.1.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 4
17.1.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 4
17.2 | Tariff metering system for 220kV OHL feeders, complete with wiring, accessories etc. and including:
17.2.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
17.2.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
17.3 | Tariff metering system for Auto-Transformer, complete with wiring, accessories etc. and including:
17.3.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
17.3.2 | Check Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
17.4 | Tariff metering system for LVAC incomer panels, complete with wiring, accessories etc. and including:
17.4.1 | Main Meter including Watthour-meter (Multi tariff), Varhour-meter (Multi tariff), with 0.2 class accuracy | No. | 2
17.5 | Metering data collection and communication system, complete with fibre optic cabling, accessories, each kind of energy meters software and communication ports. All media and accessories in order to transferring energy meter measured values to remote center according to both KETRACO and KPLC required specification. | Lot | 1
17.6 | Metering panel with all accessories and auxiliaries, lighting, heating, socket, wiring, terminals, test facilities, and all other switches, labels, test block/plug , Labels, etc. | No. | 3
17.7 | All other related relays, racks, Voltage/Current test block, cubicles, terminals, As needed to complete the metering system. | Lot | 1
17.8 | TOTAL PRICE ITEM 17
18 | FAULT MONITORING SYSTEM & PMU
18.1 | Fault and Event Monitoring System | Lot | 1
18.2 | Phasor Mesurment Unit (PMU) system with Separate GPS, Ethernet Switch, Industrial PC | Lot | 1
18.3 | Data Aquisition Units | Lot | 1
18.4 | Master Station | No. | 1
18.5 | Local HMI | No. | 1
18.7 | Fault and Event Recorder Panel with all accessories such as wiring, Lighting, heater, socket, terminal, Indication lamp, transducer, control equipment, monitor, keyboard, mouse, case, printer, I/O card and etc.(all requirements for future extension must be considered) | Lot | 1
18.8 | Phasor Mesurment Unit Panel with all accessories such as wiring, Lighting, heater, socket, terminal, Indication lamp, transducer, control equipment, monitor, keyboard, mouse, case, printer, I/O card and etc.(all requirements for future extension must be considered) | Lot | 1
18.9 | TOTAL PRICE ITEM 18
19 | MISCELLANEOUS
19.1 | Padlocks / Keys (for panels, outdoor equipments, doors, etc.) | Lot | 1
19.2 | Equipment/Bay labels, safety warning plates, road signages, room name plates, etc. | Lot | 1
19.3 | Bay Marshalling Kiosk | Lot | 1
19.4 | CCTV System with all ralated equipment for indoor and outdoor, including Cameras of suitable type and required specifications with poles, recorder, storage, monitor, switch, cabling, boxes, fixings, brackets and etc. (acc. to technical specifications in part 2-B) | Lot | 1
19.5 | Employer Communication
19.5.1 | 10 Mobile phones and airtime for Type 1 as specified in bid document | Lot | 1
19.5.2 | 10 Mobile phones and airtime for Type 2 as specified in bid document | Lot | 1
19.6 | Softwares and Licences as listed below and as per Part 2A AutoCAD for windows STAAD Pro DIgSILENT DIALux BIM software | Lot | 1
19.7 | Any other item not included above but required to complete the project successfully. (Tenderer shall specify and include breakdown of price in his proposal) | Lot | 1
19.8 | TOTAL PRICE ITEM 19
20 | Mobilization, Site Transport, Site Office and Permanent Living Provision as per Employer's Requirements, Clause 31, 32 & 34 of Part 2-A of Employer's Requirements
20.1 | Vehicles as per part 2-A
20.1.1 | Operation, maintenance, regular upkeep of the vehicles including spares, consumables and services of driver/mechanic experienced in desert driving, insurance etc. for the entire duration of the contract as per Part 2-A | Lot | 1
20.2 | Temporary Works, Site Offic, Site Storage and Living Accomodation as per Part 2-A
20.2.1 | Mobilization including all required equipment, machineries, devices, tools and facilities as specified in Clause 2.6 of section III of Part1 and Part 2-A | Lot | 1
20.2.2 | Site Office fully equipped/furnished as specified in the Employer's Requirements and with fully furnished kitchenettes, Storage Facilities as per Part 2-A | Lot | 1
20.2.3 | Site power supply from local power network, etc. | Lot | 1
20.2.4 | Site temporary fencing with barbed wire | Lot | 1
20.2.5 | Project sign boards | Lot | 1
20.2.6 | Roads, sidewalks and parking | Lot | 1
20.2.7 | Road, fence and area lighting system with all ralated equipment including Lighting fixture and terminal boxes, Steel lighting poles with related terminals, cables, fuses, fixtures, lamps, related accessories and AC distribution outdoor cubicles | Lot | 1
20.2.8 | Landscaping including maintenance during entire duration of contract | Lot | 1
20.2.9 | Storage facilities | Lot | 1
20.2.10 | First aid facilities | Lot | 1
20.2.11 | Ambulance facilities | Lot | 1
20.2.12 | Drainage system | Lot | 1
20.2.13 | Sewage system | Lot | 1
20.2.14 | Water supply system | Lot | 1
20.2.15 | Site Toilets | Lot | 1
20.2.16 | Watch and ward and access control to site during construction | Lot | 1
20.2.17 | Site Internet connection and facilities | Lot | 1
20.3 | Staff Housings for Permanent Living of Technical and Security Personnel as per Clause 31 of Part 2-A
20.3.1 | Technical staff Housing Civil works (including Excavation, concrete works, backfilling, and etc.) together with building services e.g. Lighting, Small Power System, Water Supply and Sewage System, HVAC (DX split units, fans, etc.), Water Solar Heating, Fire Detection and hand held fire extinguishers,fire blankets, fully furnished | Units | 4
20.3.1.1 | Construction of Technical staff Housing (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System, Water Supply and Sewage System, access control, etc. Acc. to bid drawings | m^2 | 420
20.3.1.2 | Complete Split Unit, 9000 BTU/hr for Bedrooms | NO. | 8
20.3.1.3 | Complete Split Unit, 12000 BTU/hr for Living and Dining Rooms | NO. | 8
20.3.1.4 | Exhaust Fan, 270 m3/hr for Toilets | NO. | 4
20.3.1.5 | Hood-450 CFM for Kitchen | NO. | 4
20.3.1.6 | Dry-Powder Fire extinguishers, 12 Kg for Bedrooms, Living and Dining Room | No. | 12
20.3.1.7 | CO2 Fire extinguishers, 6 Kg for Bedrooms, Living and Dining Room | No. | 12
20.3.1.8 | Solar Water Heater with backup electric heating element | No. | 4
20.3.1.9 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
20.3.1.10 | Other furniture and devices and facilities as in bid documents (furniture, TV, wi-fi, IP phone, refrigrator, freezer, oven, hood, electric cookers gas cooker, water filter, etc.) | Lot | 1
20.3.2 | Security staff Housing Civil work (including Excavation, concrete works, backfilling, and etc.) together with building services e.g. Lighting, Small Power System, Water Supply and Sewage System, HVAC (DX split units, fans, etc.), Water Solar Heating, Fire Detection and hand held fire extinguishers,fire blankets, fully furnished | Units | 4
20.3.2.1 | Construction of Security staff Housing (including Excavation, concrete works, backfilling, and etc.) and Building services such as Lighting, Small Power System, Water Supply and Sewage System, access control, etc. Acc. to bid drawings | m^2 | 112
20.3.2.2 | Complete Split Unit,18000 BTU/hr for Staff Rooms | No. | 4
20.3.2.3 | Exhaust Fan, 270 m3/hr for Toilets | No. | 4
20.3.2.4 | Hood-450 CFM for Kitchen | No. | 4
20.3.2.5 | Dry-Powder Fire extinguishers, 12 Kg for Staff Rooms | No. | 4
20.3.2.6 | CO2 Fire extinguishers, 6 Kg for Staff Rooms | No. | 4
20.3.2.7 | Solar Water Heater with backup electric heating element | No. | 2
20.3.2.8 | All Other Mechanical/ Electrical/ Plumbing Installations (including Shower, Faucet, Basin, Sink, Eye Wash, Ceramic Floor Mounted Toilet, Pipes, Valves, etc.) | Lot | 1
20.3.2.9 | Other furniture and devices and facilities as in bid document (T.V, refrigrator, freezer, oven, hood, IP phone, etc.) | Lot | 1
20.3.3 | Boundary fence for the staff housings | Lot | 1
20.3.4 | Decorative gate for person entry at the staff housings | No. | 1
20.5 | Cable TV network | Lot | 1
20.6 | Site Internet facilities | Lot | 1
20.7 | Diesel Generator 200kVA including generator control and protection panel and all peripheral equipment, reservior(s), and accessories for Technical and Security Staff Housing. including a shed for the generator set. | Lot | 1
20.7 | TOTAL PRICE ITEM 20
21 | FACTORY ACCEPTANCE TESTS
Provision as per Employers Requirements: - Part 2-A, - Part 2-B, Relevant Clauses for Testing and Inspection
21.1 | Auto Transformers FAT | Lot | 1
21.2 | Earthing & Auxiliary transformers FAT | Lot | 1
21.3 | NER FAT | Lot | 1
21.4 | Instrument Transformers FAT | Lot | 1
21.5 | Circuit Breakers FAT | Lot | 1
21.6 | Disconnectors & Earth Switches FAT | Lot | 1
21.7 | Surge Arrestors FAT | Lot | 1
21.8 | Conductors, Shield Wires, OPGW, clamps and connectors FAT | Lot | 1
21.9 | Post and String Insulators FAT | Lot | 1
21.10 | Cables FAT | Lot | 1
21.11 | Protection, Control & Metering Panels FAT | Lot | 1
21.12 | Substation Automation and Control System FAT | Lot | 1
21.13 | Telecommunication Equipment FAT | Lot | 1
21.14 | Fault Monitoring System FAT | Lot | 1
21.15 | Phasor Measurement Units FAT | Lot | 1
21.16 | 110Vdc, 48Vdc Batteries, Battery Chargers and UPS FAT | Lot | 1
21.17 | AC and DC Distribution Panels FAT | Lot | 1
2.1.18 | Solar PV Modules, Charge Controllers, Hybrid Inverters and Batteries for Outdoor and Indoor lighting and associated panels/switchgears and accessories | Lot | 1
21.19 | Gantries, Steel Structures and Accessories FAT | Lot | 1
21.21 | Other Equipment's FAT as required | Lot | 1
21.22 | TOTAL PRICE ITEM 21
22 | TRAINING
Provision as per bid document of Part 2-A of Employers Requirements
22.1 | Equipment Sizing, Design and Calculations (4 Engineers for 3 weeks) | Lot | 1
22.2 | Protection and Control for Electrical Power Systems (4 Engineers for 3 weeks) | Lot | 1
22.3 | Power System Analysis (4 Engineers for 2 weeks) | Lot | 1
22.4 | Communication & Substation Control System – Application & Design (4 Engineers for 2 weeks) | Lot | 1
22.5 | Civil Engineering (4 Engineers for 3 weeks) | Lot | 1
22.6 | Operations & Maintenance (4 Technicians for 2 weeks) | Lot | 1
22.7 | Substation site Operation and Maintenance (20 Engineers for 4 weeks) | Lot | 1
22.8 | PMU, PDC and Wide-Area Monitoring System (5 Engineers for 3 weeks) | Lot | 1
22.11 | TOTAL PRICE ITEM 22
23 | INTERNSHIP and EMPLOYMENT
Provision as per bid documents ,Part 2-A of Employers Requirements
23.1 | Student Internship for the entire duration of the contract | No. | 10
23.2 | Graduates Employment for the entire duration of the contract | No. | 2
23.3 | TOTAL PRICE ITEM 23
24 | SITE ACCEPTANCE TEST, PRE-COMMISSIONING, COMMISSIONING AND END-TO-END TESTING
24.1 | Substation Site Acceptance Test, Pre-commissioning, commissioning, and also end-to-end testing including NCC/RCC/NSCC signaling and remote end relay settings modifications and associated testing and commissioning | Lot | 1
24.2 | TOTAL PRICE ITEM 24
25 | TOTAL PRICE SCHEDULE 4A KIMUKA SUBSTATION Note: Contractor shall include and consider all activities which are necessary to complete the project works (including construction, erection, installation, mobilization, site transportation and accomodation, modification, replacement, relocation, tests, pre-commissioning, commissioning, training, internship and etc. as required)
Note on C215: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease clarify which software. Reply: This under SAS , so this refers to software SAS software installation
Note on D580: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: lump sum. ??? Reply: These items are included to take care of site differences especially in site levels. Lump sum unit price negates this purpose. Our approach has been to remeasure the specific quantities at site.

## Schedule 1B_TL
SCHEDULE NO. 1B
PLANT, EQUIPMENT AND MANDATORY SPARES SUPPLIED FROM ABROAD
FOR KIMUKA TRANSMISSION LINES
1 | 2 | 3 | 4 | 5 | 6 | 7
Item No | Description | Country of Origin | Unit | Estimated Quantity | Foreign Currency (FC1) = | Total Price
[5 empty] | Foreign Manufacture | Foreign Manufacture
[5 empty] | Unit Price (CIP) | (Quantity x Unit Price)
[5 empty] | FC1 | FC1
1 | Tower Grounding
Tower Earthing / grounding as per technical specifications including counterpoise cables, earthing rods, compression jointing; connection to tower etc
1.1 | Basic tower earthing, Type A |  | per tower | 8
1.2 | Additional tower earthing, Type B |  | per tower | 2
1.3 | Additional tower earthing, Type C |  | per tower | 2
1.4 | Additional tower earthing, Type D |  | per tower | 2
1.5 | Fence earthing |  | Set | 5
2 | STEEL TOWERS with stub
SELF-SUPPORTING STEEL TOWERS, COMPLETE WITH ALL PLATES, SAFETY DEVICES, FITTINGS, BOLTS, NUTS AND ACCESSORIES Notes: 1. Quoted prices for items 2.03 to 2.06, 2.14 to 2.17, 2.25 to 2.28, 2.36 to 2.39,and 2.47 to 2.50 shall relate only the applicable 3m-, 6m-,9m- and 12m-body extensions for the respective towers as given in the outline drawing and not including complete basic tower with extensions. 2. Quoted prices 2.07 to 2.10, 2.18 to 2.21, 2.29 to 2.32, 2.40 to 2.43, and 2.51 to 2.54 shall relate only the respective 1m-, 2m-, 3m- and 4m-leg extensions for the subject towers as given in the outline drawing.
Towers Type 400S (0-2°)
2.01 | Type S tower, basic tower (includes ±0m LE) |  | Tower | 2
2.02 | Type S tower, complete basic tower - 3m |  | Tower | 1
2.03 | Type S tower , 3m Body extension |  | Tower | 1
2.04 | Type S tower , 6m Body extension |  | Tower | 1
2.05 | Type S tower , 9m Body extension |  | Tower | 1
2.06 | Type S tower , 12m Body extension |  | Tower | 1
2.07 | Type S tower , 1m Leg extension |  | each | 1
2.08 | Type S tower , 2m Leg extension |  | each | 1
2.09 | Type S tower , 3m Leg extension |  | each | 1
2.1 | Type S tower , 4m Leg extension |  | each | 1
2.11 | Stubs complete with stub extensions, cleats, nut and bolts |  | each | 12
Towers Type 400T10 (0-10°)
2.12 | Type T10 tower, basic tower (includes ±0m LE) |  | Tower | 1
2.13 | Type T10 tower, complete basic tower - 3m |  | Tower | 1
2.14 | Type T10 tower , 3m Body extension |  | Tower | 1
2.15 | Type T10 tower , 6m Body extension |  | Tower | 1
2.16 | Type T10 tower , 9m Body extension |  | Tower | 1
2.17 | Type T10 tower , 12m Body extension |  | Tower | 1
2.18 | Type T10 tower , 1m Leg extension |  | each | 1
2.19 | Type T10 tower , 2m Leg extension |  | each | 1
2.2 | Type T10 tower , 3m Leg extension |  | each | 1
2.21 | Type T10 tower , 4m Leg extension |  | each | 1
2.22 | Stubs complete with stub extensions, cleats, nut and bolts |  | each | 8
Towers Type 400T30 (10-30°)
2.23 | Type T30 tower, basic tower (includes ±0m LE) |  | Tower | 1
2.24 | Type T30 tower, complete basic tower - 3m |  | Tower | 1
2.25 | Type T30 tower , 3m Body extension |  | Tower | 1
2.26 | Type T30 tower , 6m Body extension |  | Tower | 1
2.27 | Type T30 tower , 9m Body extension |  | Tower | 1
2.28 | Type T30 tower , 12m Body extension |  | Tower | 1
2.29 | Type T30 tower , 1m Leg extension |  | each | 1
2.3 | Type T30 tower , 2m Leg extension |  | each | 1
2.31 | Type T30 tower , 3m Leg extension |  | each | 1
2.32 | Type T30 tower , 4m Leg extension |  | each | 1
2.33 | Stubs complete with stub extensions, cleats, nut and bolts |  | each | 8
Towers Type 400T60 (30-60°)
2.34 | Type T60 tower, basic tower (includes ±0m LE) |  | Tower | 2
2.35 | Type T60 tower, complete basic tower - 3m |  | Tower | 1
2.36 | Type T60 tower , 3m Body extension |  | Tower | 1
2.37 | Type T60 tower , 6m Body extension |  | Tower | 1
2.38 | Type T60 tower , 9m Body extension |  | Tower | 1
2.39 | Type T60 tower , 12m Body extension |  | Tower | 1
2.4 | Type T60 tower , 1m Leg extension |  | each | 1
2.41 | Type T60 tower , 2m Leg extension |  | each | 1
2.42 | Type T60 tower , 3m Leg extension |  | each | 1
2.43 | Type T60 tower , 4m Leg extension |  | each | 1
2.44 | Stubs complete with stub extensions, cleats, nut and bolts |  | each | 12
'Towers Type 400T90/TRM (60-90°/ 0-45°)
2.45 | Type T90/Ttrm tower, basic tower (includes ±0m LE) |  | Tower | 3
2.46 | Type T90/Ttrm tower, complete basic tower - 3m |  | Tower | 1
2.47 | Type T90/Ttrm tower , 3m Body extension |  | Tower | 1
2.48 | Type T90/Ttrm tower , 6m Body extension |  | Tower | 1
2.49 | Type T90/Ttrm tower , 9m Body extension |  | Tower | 1
2.5 | Type T90/Ttrm tower , 12m Body extension |  | Tower | 1
2.51 | Type T90/Ttrm tower , 1m Leg extension |  | each | 1
2.52 | Type T90/Ttrm tower , 2m Leg extension |  | each | 1
2.53 | Type T90/Ttrm tower , 3m Leg extension |  | each | 1
2.54 | TypeT90/Ttrm tower , 4m Leg extension |  | each | 1
2.55 | Stubs complete with stub extensions, cleats, nut and bolts |  | each | 16
2.56 | Tower Obstruction Lighting complete including power supply, according to ICAO regulations, or other method, eg inductive, details to be provided. |  | per tower | 2
2.57 | Tower Obstruction Lighting complete including independent solar power supply, according to ICAO regulations. |  | per tower | 2
2.58 | Aircraft warning spheres 60cm diameter |  | each | 30
3 | LINE CONDUCTOR INSULATORS AND FITTINGS
Supply of Complete Insulator String assembly Sets including insulators and all fittings between tower and Conductor ( Suitable for triple ACSR "condor" conductor), including but not limited to all types of clamps, hardware, extension links, armor rods, counterweights, and all connections to Towers.
3.01 | Single Suspension String (210 KN) |  | Set | 12
3.02 | Double Suspension String (210 KN) |  | Set | 6
3.03 | Double Tension String (420 KN) |  | Set | 24
3.04 | Single Tension String (210 KN) |  | Set | 120
3.05 | Single Jumper Insulator 120 KN (Pilot Susp String) |  | Set | 18
3.06 | Spacer damper for triple ACSR 'Condor' Conductor |  | Set | 300
3.07 | Spacer for triple ACSR 'Condor' Conductor (for jumper loop) |  | Set | 84
3.08 | Vibration dampers |  | Set | 168
3.09 | Mid Span Joints |  | Set | 2
3.1 | Repair Sleeve |  | Set | 2
3.11 | Counterweights for suspension strings
| a) 40 kg |  | each | 9.6
| b) 80 kg |  | each | 14.4
4 | OPGW FITTINGS AND ACCESSORIES
Supply of complete Sets of OPGW Fittings, including but not limited to all types of hardware fittings, clamps, extension links, armor rods, counterweights, earth bonds and all connections to Towers.
4.01 | Suspension set for OPGW |  | Set | 3
4.02 | Double dead end set passing for OPGW (complete set for both sides of crossarm as per attached drowings) |  | Set | 3
4.03 | Splicing tension assembly for OPGW (complete set for both sides of crossarm as per attached drowings) |  | Set | 4
4.04 | OPGW Joint Box 2 way |  | Set | 1
4.05 | OPGW Joint Box 3 way |  | Set | 1
4.06 | OPGW Joint Box 4 way |  | Set | 2
4.07 | Vibration dampers |  | Set | 14
5 | ACS Shield wire FITTINGS AND ACCESSORIES
Supply of complete Sets of ACS Fittings, including but not limited to all types of hardware fitings, clamps, extension links, armor rods, counterweights, earth bonds and all connections to Towers.
5.01 | Suspension Assembly |  | Set | 3
5.02 | Tension Assembly (complete set for both sides of crossarm as per attached drowings) |  | Set | 7
5.03 | Vibration Dampers |  | Set | 14
5.04 | Mid Span Joints |  | Set | 1
6 | CONDUCTOR AND GROUND WIRES
Supply of conductors and optical groundwire including all joints, sleeves, jumper loops, spacers and necessary dampers, earthing connections and all downleads inclusive of requisite accessories to facilitate transmission line termination on the substation gantries
6.01 | ACSR Conductor Code Name "Condor" for the double circuit; 3 phases per circuit, triple bundle conductor per phase Note: Allowances for sagging, jumpers etc within the line and at substation ends shall be part of the quoted contract price per km of line route length. |  | route km | 2.5
6.02 | Optical Groundwire (OPGW) including all splicing and connections to joint boxes Note: Allowances for sagging, splicing as well as slacks allowed for maintenance purposes within the line and at substation ends shall be part of the quoted contract price per km of line route length. |  | route km | 2.5
6.03 | ACS Shield wire 7/3.26 mm Note: Allowances for sagging, jumpers et c within the line and at substation ends shall be part of the quoted contract price per km of line route length. |  | route km | 2.5
7 | ERS TOWER SET
7.1 | Suspension ERS Tower Set including modular tower/structure, foundation/base plate, insulators along with hardware fittings, container, anchors assemblies suitable for project soil condition, guy wire and accessories, installation and construction tools and other required equipment |  | set | 4
7.2 | Tension ERS Tower Set including modular tower/structure, foundation/base plate, insulators along with hardware fittings, container, anchors assemblies suitable for project soil condition, guy wire and accessories, installation and construction tools and other required equipment |  | set | 8
8 | TOWER TYPE TESTS
Tower type tests to destruction including supply, erection, recovery including all related costs as per employer requirements
8.1 | Tower Type S (Basic Tower + 12m BE + 4m LE) |  | Per tower | 1
Tower type test to ultimate loading including supply, erection, dismantling, recovery including all related costs as per employer requirements
8.2 | Tower Type T10 (Basic Tower + 12m BE + 4m LE) |  | Per tower | 1
8.3 | Tower type T30 (Basic Tower + 12m BE + 4m LE) |  | Per tower | 1
8.4 | Tower type T60 (Basic Tower + 12m BE + 4m LE) |  | Per tower | 1
8.5 | Tower type T90/Ttrm (Basic Tower + 12m BE + 4m LE) |  | Per tower | 1
TOTAL PRICE SCHEDULE 1B KIMUKA TRANSMISSION LINE
Note on G7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease see comment in PS 1A SS Reply: addressed
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: number of grounding of tower is inconsistent with the number of tower. Please clarify the numbers of steel towers in item 2. The line length is short , but big number of towers in the PS. Therefore, please change 1 to 0 if the tower is only tentative/ provisional. Reply: The tower grounding and the number of towers match in terms of quantity. Type D tower earthing shall be used where type C is insufficient. All other tower quantities refer to the body and leg extensions. Since tower spotting has not been finalised, a rate is required to avoid any price escalations during project implementation.
Note on C116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please clarify 6 phase. the linre is 3 phase, triple bundle, double circuit???? Reply: Amended and made clearer

## Schedule 2B_TL
SCHEDULE NO. 2B
PLANT, EQUIPMENT AND MANDATORY SPARES SUPPLIED FROM WITHIN EMPLOYERS COUNTRY
FOR KIMUKA TRANSMISSION LINES
1 | 2 | 3 | 4 | 5 | 6
Item No | Description | Unit | Estimated Quantity | Local Currency (KSh) = KENYAN SHILLINGS | Total Price
|  |  |  | Local Manufacture | Local Manufacture
|  |  |  | Unit Price (DAP) | (Quantity x Unit Price)
|  |  |  | KSh | KSh
1 | Tower Grounding
Tower Earthing / grounding as per technical specifications including counterpoise cables, earthing rods, compression jointing; connection to tower etc
1.1 | Basic tower earthing, Type A | per tower | 8
1.2 | Additional tower earthing, Type B | per tower | 2
1.3 | Additional tower earthing, Type C | per tower | 2
1.4 | Additional tower earthing, Type D | per tower | 2
1.5 | Fence earthing | Set | 5
2 | STEEL TOWERS with stub
SELF-SUPPORTING STEEL TOWERS, COMPLETE WITH ALL PLATES, SAFETY DEVICES, FITTINGS, BOLTS, NUTS AND ACCESSORIES Notes: 1. Quoted prices for items 2.03 to 2.06, 2.14 to 2.17, 2.25 to 2.28, 2.36 to 2.39,and 2.47 to 2.50 shall relate only the applicable 3m-, 6m-,9m- and 12m-body extensions for the respective towers as given in the outline drawing and not including complete basic tower with extensions. 2. Quoted prices 2.07 to 2.10, 2.18 to 2.21, 2.29 to 2.32, 2.40 to 2.43, and 2.51 to 2.54 shall relate only the respective 1m-, 2m-, 3m- and 4m-leg extensions for the subject towers as given in the outline drawing.
Towers Type 400S (0-2°)
2.01 | Type S tower, basic tower (includes ±0m LE) | Tower | 2
2.02 | Type S tower, complete basic tower - 3m | Tower | 1
2.03 | Type S tower , 3m Body extension | Tower | 1
2.04 | Type S tower , 6m Body extension | Tower | 1
2.05 | Type S tower , 9m Body extension | Tower | 1
2.06 | Type S tower , 12m Body extension | Tower | 1
2.07 | Type S tower , 1m Leg extension | each | 1
2.08 | Type S tower , 2m Leg extension | each | 1
2.09 | Type S tower , 3m Leg extension | each | 1
2.1 | Type S tower , 4m Leg extension | each | 1
2.11 | Stubs complete with stub extensions, cleats, nut and bolts | each | 12
Towers Type 400T10 (0-10°)
2.12 | Type T10 tower, basic tower (includes ±0m LE) | Tower | 1
2.13 | Type T10 tower, complete basic tower - 3m | Tower | 1
2.14 | Type T10 tower , 3m Body extension | Tower | 1
2.15 | Type T10 tower , 6m Body extension | Tower | 1
2.16 | Type T10 tower , 9m Body extension | Tower | 1
2.17 | Type T10 tower , 12m Body extension | Tower | 1
2.18 | Type T10 tower , 1m Leg extension | each | 1
2.19 | Type T10 tower , 2m Leg extension | each | 1
2.2 | Type T10 tower , 3m Leg extension | each | 1
2.21 | Type T10 tower , 4m Leg extension | each | 1
2.22 | Stubs complete with stub extensions, cleats, nut and bolts | each | 8
Towers Type 400T30 (10-30°)
2.23 | Type T30 tower, basic tower (includes ±0m LE) | Tower | 1
2.24 | Type T30 tower, complete basic tower - 3m | Tower | 1
2.25 | Type T30 tower , 3m Body extension | Tower | 1
2.26 | Type T30 tower , 6m Body extension | Tower | 1
2.27 | Type T30 tower , 9m Body extension | Tower | 1
2.28 | Type T30 tower , 12m Body extension | Tower | 1
2.29 | Type T30 tower , 1m Leg extension | each | 1
2.3 | Type T30 tower , 2m Leg extension | each | 1
2.31 | Type T30 tower , 3m Leg extension | each | 1
2.32 | Type T30 tower , 4m Leg extension | each | 1
2.33 | Stubs complete with stub extensions, cleats, nut and bolts | each | 8
Towers Type 400T60 (30-60°)
2.34 | Type T60 tower, basic tower (includes ±0m LE) | Tower | 2
2.35 | Type T60 tower, complete basic tower - 3m | Tower | 1
2.36 | Type T60 tower , 3m Body extension | Tower | 1
2.37 | Type T60 tower , 6m Body extension | Tower | 1
2.38 | Type T60 tower , 9m Body extension | Tower | 1
2.39 | Type T60 tower , 12m Body extension | Tower | 1
2.4 | Type T60 tower , 1m Leg extension | each | 1
2.41 | Type T60 tower , 2m Leg extension | each | 1
2.42 | Type T60 tower , 3m Leg extension | each | 1
2.43 | Type T60 tower , 4m Leg extension | each | 1
2.44 | Stubs complete with stub extensions, cleats, nut and bolts | each | 12
'Towers Type 400T90/TRM (60-90°/ 0-45°)
2.45 | Type T90/Ttrm tower, basic tower (includes ±0m LE) | Tower | 3
2.46 | Type T90/Ttrm tower, complete basic tower - 3m | Tower | 1
2.47 | Type T90/Ttrm tower , 3m Body extension | Tower | 1
2.48 | Type T90/Ttrm tower , 6m Body extension | Tower | 1
2.49 | Type T90/Ttrm tower , 9m Body extension | Tower | 1
2.5 | Type T90/Ttrm tower , 12m Body extension | Tower | 1
2.51 | Type T90/Ttrm tower , 1m Leg extension | each | 1
2.52 | Type T90/Ttrm tower , 2m Leg extension | each | 1
2.53 | Type T90/Ttrm tower , 3m Leg extension | each | 1
2.54 | TypeT90/Ttrm tower , 4m Leg extension | each | 1
2.55 | Stubs complete with stub extensions, cleats, nut and bolts | Tower | 16
2.56 | Tower Obstruction Lighting complete including power supply, according to ICAO regulations, or other method, eg inductive, details to be provided. | Tower | 2
2.57 | Tower Obstruction Lighting complete including independent solar power supply, according to ICAO regulations. | Tower | 2
2.58 | Aircraft warning spheres 60cm diameter | each | 30
3 | LINE CONDUCTOR INSULATORS AND FITTINGS
Supply of Complete Insulator String Assembly Sets including insulators and all fittings between tower and Conductor ( Suitable for triple ACSR "condor" conductor), including but not limited to all types of clamps, hardware, extension links, armor rods, counterweights, and all connections to Towers.
3.01 | Single Suspension String (210 KN) | Set | 12
3.02 | Double Suspension String (210 KN) | Set | 6
3.03 | Double Tension String (420 KN) | Set | 24
3.04 | Single Tension String (210 KN) | Set | 120
3.05 | Single Jumper Insulator 120 KN (Pilot Susp String) | Set | 18
3.06 | Spacer damper for triple ACSR 'Condor' Conductor | Set | 300
3.07 | Spacer for triple ACSR 'Condor' Conductor (for jumper loop) | Set | 84
3.08 | Vibration dampers | Set | 168
3.09 | Mid Span Joints | Set | 2
3.1 | Repair Sleeve | Set | 2
3.11 | Counterweights for suspension strings
| a) 40 kg | each | 10
| b) 80 kg | each | 14
4 | OPGW FITTINGS AND ACCESSORIES
Supply of complete Sets of OPGW Fittings, including but not limited to all types of hardware fittings, clamps, extension links, armor rods, counterweights, earth bonds and all connections to Towers.
4.01 | Suspension set for OPGW | Set | 3
4.02 | Double dead end set passing for OPGW (complete set for both sides of crossarm as per attached drowings) | Set | 3
4.03 | Splicing tension assembly for OPGW (complete set for both sides of crossarm as per attached drowings) | Set | 4
4.04 | OPGW Joint Box 2 way | Set | 1
4.05 | OPGW Joint Box 3 way | Set | 1
4.06 | OPGW Joint Box 4 way | Set | 2
4.07 | Vibration dampers | Set | 14
5 | ACS Shield wire FITTINGS AND ACCESSORIES
Supply of complete Sets of Fittings, including all types of clamps, extension links, armor rods, tower bonding clamps and all connections to Tower.
5.01 | Suspension Assembly | Set | 3
5.02 | Tension Assembly (complete set for both sides of crossarm as per attached drowings) | Set | 7
5.03 | Vibration Dampers | Set | 14
5.04 | Mid Span Joints | Set | 1
6 | CONDUCTOR AND GROUND WIRES
Supply of conductors and optical groundwire including all joints, sleeves, jumper loops, spacers and necessary dampers, earthing connections and all downleads inclusive of requisite accessories to facilitate transmission line termination on the substation gantries
6.01 | ACSR Conductor Code Name "Condor" for the double circuit; 3 phases per circuit, triple bundle conductor per phase Note: Allowances for sagging, jumpers etc within the line and at substation ends shall be part of the quoted contract price per km of line route length. | route km | 2.5
6.02 | Optical Groundwire (OPGW) including all splicing and connections to joint boxes Note: Allowances for sagging, splicing as well as slacks allowed for maintenance purposes within the line and at substation ends shall be part of the quoted contract price per km of line route length. | route km | 2.5
6.03 | ACS Shield wire 7/3.26 mm Note: Allowances for sagging, jumpers et c within the line and at substation ends shall be part of the quoted contract price per km of line route length. | route km | 2.5
7 | ERS TOWER SET
7.1 | Suspension ERS Tower Set including modular tower/structure, foundation/base plate, insulators along with hardware fittings, container, anchors assemblies suitable for project soil condition, guy wire and accessories, installation and construction tools and other required equipment | set | 4
7.2 | Tension ERS Tower Set including modular tower/structure, foundation/base plate, insulators along with hardware fittings, container, anchors assemblies suitable for project soil condition, guy wire and accessories, installation and construction tools and other required equipment | set | 8
8 | TOWER TYPE TESTS
Tower type tests to destruction including supply, erection, recovery including all related costs as per employer requirements
8.1 | Tower Type S (Basic Tower + 12m BE + 4m LE) | Per tower | 1
Tower type test to ultimate loading including supply, erection, dismantling, recovery including all related costs as per employer requirements
8.2 | Tower Type T10 (Basic Tower + 12m BE + 4m LE) | Per tower | 1
8.3 | Tower type T30 (Basic Tower + 12m BE + 4m LE) | Per tower | 1
8.4 | Tower type T60 (Basic Tower + 12m BE + 4m LE) | Per tower | 1
8.5 | Tower type T90/Ttrm (Basic Tower + 12m BE + 4m LE) | Per tower | 1
TOTAL PRICE SCHEDULE 2B KIMUKA TRANSMISSION LINE
Note on C116: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please clarify 6 phase. the linre is 3 phase, triple bundle, double circuit???? Reply: Amended and made clearer

## Schedule 3B_TL
SCHEDULE NO. 3B
DESIGN SERVICES
FOR KIMUKA TRANSMISSION LINES
1 | 2 |  | 3 | 5 | 6
Item No | Description | Unit | Estimated Quantity | Foreign Currency (FC1) = | Total Price
|  |  |  | Design Services | Design Services
|  |  |  | Unit Price | (Quantity x Unit Price)
|  |  |  | FC1 | FC1
1 | DESIGN SERVICES
1.1 | Tower Design | lump sum | 1
1.2 | ERS design (tower, foundation and all related equipment, as well as installation manual and training) including type tests | lump sum | 1
1.3 | Foundation Design | lump sum | 1
1.4 | Conductor, shield wire and OPGW Design including hardware and fittings and type tests | lump sum | 1
1.5 | Line Profiling (preparation of plan and profile drawings, tower spotting and tower schedule in PLS-CADD software inclusive of cross diagonal profiles and any requisite foundation protection works) | lump sum | 1
1.6 | All other design works for completeness of the line design and its functionality. | lump sum | 1
TOTAL PRICE SCHEDULE 3B KIMUKA TRANSMISSION LINE

## Schedule 4B_TL
SCHEDULE NO. 4B
INSTALLATION AND OTHER SERVICES
FOR KIMUKA TRANSMISSION LINES
1 | 2 | 3 | 4 | 5 | 6
Item No | Description | Unit | Estimated Quantity | Foreign Currency (FC1) = | Total Price
|  |  |  | Installation & Other Services | Installation & Other Services
|  |  |  | Unit Price | (Quantity x Unit Price)
|  |  |  | FC1 | FC1
1.0 | GENERAL WORKS
All necessary survey activities including but not limited to survey of crossing objects including pegging of towers, diagonal profiles and all necessary documentation for the OHTL, soil investigations and route clearing & access roads.
1.1 | Mobilization costs towards contractor's storage yards and facilities | lump sum | 1
1.2 | Complete detailed profile survey and setting out of the transmision line route including preparation of plan and profile drawings, tower spotting / pegging of tower positions, check surveys and preparation of associated reports, preparation of cross-diagonal profiles for all tower locations, tower schedules etc. | route km | 2.5
1.3 | Prices for comprehensive/detailed soil investigations and tests including all overheads and earth resistance data per location as Specified | route km | 2.5
1.3.1 | Machine boring of single bore hole up to a depth of 10meters including all necessray drilling, sampling, laboratory testing of samples, the preparation of reports, including correlations with in-situ tests detailed in relevant sections of specifications and in line with recommendations for design of foundations: including all mobilisation and demobilistaion costs and all transport of equipment between tower sites (SPT) | Tower | 8
1.3.2 | Sub-soil investigations at tower locations by means of in-situ penetrometer, vane test or bearing test per spefications to determine class of foundation to be installed | lump sum | 10
1.4 | Line access / wayleave trace clearance Shall include bush clearing along the way leave trace of the transmission line route as well as requisite access roads per specifications | route km | 2.5
1.5 | Relocation / Undergrounding with underground cables of Low Voltage / Medium Voltage Distribution Power Lines. NB: Upon conclusion of plan and profile designs and these works are found necessary, they shall be undertaken as shall be advised by the Project Manager upon consultation with the owner (KPLC). KPLC usually undertakes these works upon payment and contractor shall make necessary arrangements with them.
1.5.1 | Costs towards relocation/ undergrounding of existing 66 kV lines that new line will cross or in some instances their presence would affect tower spotting or related lines operation in their O&M phase. | km | 0.5
1.5.2 | Paying for relocation/ undergrounding of existing 33 kV lines that new line will cross or in some instances their presence would affect tower spotting or related lines operation in their O&M phase. | km | 0.5
1.5.3 | Paying for relocation/ undergrounding of existing 11 kV lines that new line will cross or in some instances their presence would affect tower spotting or related lines operation in their O&M phase. | km | 0.5
1.5.4 | Paying for relocation/ undergrounding of existing 0.415 kV (below 11 kV) lines that new line will cross or in some instances their presence would affect tower spotting or related lines operation in their O&M phase. | km | 0.5
1.6 | Installation of Farm Gates to Approval | each | 3
2.0 | FOUNDATION WITH STUB
Installation of complete foundations for various Tower Types according to the specification, including but not limited to; stubs, cleats and setting, transport, excavation, installation of stubs, all necessary reinforcement, shuttering, concreting, backfilling, compacting, complete tower earthing and their connections to tower, measuring of earth resistance and submitting of records to Employer / Engineer, according to drawings and regulations of the Employer. Soil class definition according to permissible soil pressure and in agreement with the design and specifications. Price of all required material i.e concrete and steel reinforcement is deemed included
Complete Foundation Works for Type 400S (0-2°) Tower
2.01 | Class 1 (rock) | Tower | 1
2.02 | Class 2 Pad and Chimney | Tower | 1
2.03 | Class 3 Pad and Chimney | Tower | 1
2.04 | Class 4 Pad and Chimney | Tower | 1
2.05 | Class 4W Pad and Chimney | Tower | 1
2.06 | Class 5 Pad and Chimney | Tower | 1
2.07 | Class 5W Pad and Chimney | Tower | 1
Complete Foundation Works for Type 400T10 (0-10°) Tower
2.08 | Class 1 (rock) | Tower | 1
2.09 | Class 2 Pad and Chimney | Tower | 1
2.1 | Class 3 Pad and Chimney | Tower | 1
2.11 | Class 4 Pad and Chimney | Tower | 1
2.12 | Class 4W Pad and Chimney | Tower | 1
2.13 | Class 5 Pad and Chimney | Tower | 1
2.14 | Class 5W Pad and Chimney | Tower | 1
Complete Foundation Works for Type 400T30 (10-30°) Tower
2.15 | Class 1 (rock) | Tower | 1
2.16 | Class 2 Pad and Chimney | Tower | 1
2.17 | Class 3 Pad and Chimney | Tower | 1
2.18 | Class 4 Pad and Chimney | Tower | 1
2.19 | Class 4W Pad and Chimney | Tower | 1
2.2 | Class 5 Pad and Chimney | Tower | 1
2.21 | Class 5W Pad and Chimney | Tower | 1
Complete Foundation Works for Type 400T60 (30-60°) Tower
2.22 | Class 1 (rock) | Tower | 1
2.23 | Class 2 Pad and Chimney | Tower | 1
2.24 | Class 3 Pad and Chimney | Tower | 1
2.25 | Class 4 Pad and Chimney | Tower | 1
2.26 | Class 4W Pad and Chimney | Tower | 1
2.27 | Class 5 Pad and Chimney | Tower | 1
2.28 | Class 5W Pad and Chimney | Tower | 1
Complete Foundation Works for Type 400T90/TRM (60-90°/ 0-45°) Tower
2.29 | Class 1 (rock) | Tower | 1
2.3 | Class 2 Pad and Chimney | Tower | 1
2.31 | Class 3 Pad and Chimney | Tower | 1
2.32 | Class 4 Pad and Chimney | Tower | 1
2.33 | Class 4W Pad and Chimney | Tower | 1
2.34 | Class 5 Pad and Chimney | Tower | 1
2.35 | Class 5W Pad and Chimney | Tower | 1
3 | MISCELLANEOUS PRICES FOR FOUNDATION WORKS: Special foundation works including pile caps, beams and modification to normal foundation to adapt specified foundation classes to cater for particular soil conditions. NB: These shall only be applicable to stated works that have been approved by the Employer/Employer's Representative and executed
3.01 | Stone masonry retaining wall in cement:sand (1:3) mortar | Square meter | 50
3.02 | 1m x 1m x 1m rock filled gabion installed to protect foundations against erosion | Linear Meter | 600
3.03 | Additional structural concrete (grade C25/30 per eurocode notation) including cost of formwork | cubic meter | 300
3.04 | Additional excavation including reinstatement | cubic meter | 600
3.05 | Additional steel reinforcing bars including supply, bending and placing | tonnes | 10
3.06 | Solid rock excavation excluding Class 1 foundations (including reinstatement) | cubic meter | 1000
3.07 | Rip-rap stone work, 0.5m deep over tower base to protect against erosion | Square meter | 1000
3.08 | Imported Backfill material including placement | cubic meter | 1000
4 | TOWER GROUNDING
All tower groundings including but not limited to excavation, laying of counterpoise, connection to towers including all clamps or other connections, corrosion protection, backfilling, compaction and measuring of ohmic value (regardless of the grounding type, includes any required grounding works such as fence earthing). This shall be in compliance with specifications and approved drawings
4.01 | Basic tower earthing, Type A | per tower | 8
4.02 | Additional tower earthing, Type B | per tower | 2
4.03 | Additional tower earthing, Type C | per tower | 2
4.04 | Additional tower earthing, Type D | per tower | 2
4.05 | Metallic / electric fence earthing | Set | 5
4.06 | Measurement of electrical footing resistance to earth at each tower site, including recording in an approved manner | per tower | 14
5 | STEEL TOWERS
Complete tower erection works in accordance with specifications along with approved drawings which shall include but not limited to handling, storage at site and distribution to individual sites, installation of tower accessories, anti-theft bolts etc. Securing against vandalism during construction Notes: 1. Quoted prices for items 5.1.3 to 5.1.6, 5.2.4 to 5.2.7, 5.3.5 to 5.3.8, 5.3.16, to 5.3.19, and 5.3.27 to 5.3.30 shall relate only the applicable 3m-, 6m- , 9m and 12m-body extensions for the respective towers as given in the outline drawing and not including complete basic tower with extensions. 2. Quoted prices 5.1.7 to 5.20, 5.2.8 to 5.3.1, 5.3.9 to 5.3.12, 5.3.20 to 5.3.23, and 5.3.31 to 5.3.34 shall relate only the respective 1m-, 2m-, 3m- and 4m-leg extensions for the subject towers as given in the outline drawing.
5.1 | Complete Erection Works of Type 400S (0-2°) Tower
5.1.1 | Type S tower, basic tower (includes ±0m LE) | Tower | 2
5.1.2 | Type S tower, complete basic tower - 3m | Tower | 1
5.1.3 | Type S tower , 3m Body extension | Tower | 1
5.1.4 | Type S tower , 6m Body extension | Tower | 1
5.1.5 | Type S tower , 9m Body extension | Tower | 1
5.1.6 | Type S tower , 12m Body extension | Tower | 1
5.1.7 | Type S tower , 1m Leg extension | each | 1
5.1.8 | Type S tower , 2m Leg extension | each | 1
5.1.9 | Type S tower , 3m Leg extension | each | 1
5.2 | Type S tower , 4m Leg extension | each | 1
5.2.1 | Complete Erection Works of Type 400T10 (0-10°) Tower
5.2.2. | Type T10 tower, basic tower (includes ±0m LE) | Tower | 1
5.2.3 | Type T10 tower, complete basic tower - 3m | Tower | 1
5.2.4 | Type T10 tower , 3m Body extension | Tower | 1
5.2.5 | Type T10 tower , 6m Body extension | Tower | 1
5.2.6 | Type T10 tower , 9m Body extension | Tower | 1
5.2.7 | Type T10 tower , 12m Body extension | Tower | 1
5.2.8 | Type T10 tower , 1m Leg extension | each | 1
5.2.9 | Type T10 tower , 2m Leg extension | each | 1
5.3.0 | Type T10 tower , 3m Leg extension | each | 1
5.3.1 | Type T10 tower , 4m Leg extension | each | 1
5.3.2 | Complete Erection Works of Type 400T30 (10-30°) Tower
5.3.3 | Type T30 tower, basic tower (includes ±0m LE) | Tower | 1
5.3.4 | Type T30 tower, complete basic tower - 3m | Tower | 1
5.3.5 | Type T30 tower , 3m Body extension | Tower | 1
5.3.6 | Type T30 tower , 6m Body extension | Tower | 1
5.3.7 | Type T30 tower , 9m Body extension | Tower | 1
5.3.8 | Type T30 tower , 12m Body extension | Tower | 1
5.3.9 | Type T30 tower , 1m Leg extension | each | 1
5.3.10 | Type T30 tower , 2m Leg extension | each | 1
5.3.11 | Type T30 tower , 3m Leg extension | each | 1
5.3.12 | Type T30 tower , 4m Leg extension | each | 1
5.3.13 | Complete Erection Works of Type 400T60 (30-60°) Tower
5.3.14 | Type T60 tower, basic tower (includes ±0m LE) | Tower | 2
5.3.15 | Type T60 tower, complete basic tower - 3m | Tower | 1
5.3.16 | Type T60 tower , 3m Body extension | Tower | 1
5.3.17 | Type T60 tower , 6m Body extension | Tower | 1
5.3.18 | Type T60 tower , 9m Body extension | Tower | 1
5.3.19 | Type T60 tower , 12m Body extension | Tower | 1
5.3.20 | Type T60 tower , 1m Leg extension | each | 1
5.3.21 | Type T60 tower , 2m Leg extension | each | 1
5.3.22 | Type T60 tower , 3m Leg extension | each | 1
5.3.23 | Type T60 tower , 4m Leg extension | each | 1
5.3.24 | Complete Erection Works of Type 400T90/TRM (60-90°/ 0-45°)
5.3.25 | Type T90/Ttrm tower, basic tower (includes ±0m LE) | Tower | 3
5.3.26 | Type T90/Ttrm tower, complete basic tower - 3m | Tower | 1
5.3.27 | Type T90/Ttrm tower , 3m Body extension | Tower | 1
5.3.28 | Type T90/Ttrm tower , 6m Body extension | Tower | 1
5.3.29 | Type T90/Ttrm tower , 9m Body extension | Tower | 1
5.3.30 | Type T90/Ttrm tower , 12m Body extension | Tower | 1
5.3.31 | Type T90/Ttrm tower , 1m Leg extension | each | 1
5.3.32 | Type T90/Ttrm tower , 2m Leg extension | each | 1
5.3.33 | Type T90/Ttrm tower , 3m Leg extension | each | 1
5.3.34 | TypeT90/Ttrm tower , 4m Leg extension | each | 1
5.4 | Painting of towers for day marking of aerial obstructions (in bands of white and red including all necessary material) according to specification and ICAO recommendations. | Tower | 1
5.41 | Tower Obstruction Lighting complete including power supply, according to ICAO regulations, or other method, eg inductive, details to be provided. | Tower | 2
5.42 | Tower Obstruction Lighting complete including independent solar power supply, according to ICAO regulations. | Tower | 2
5.43 | Aircraft warning spheres 60cm diameter | each | 30
5.44 | Provision of temporary backstays to accommodate temporary termination of conductors on tension towers. | Lumpsum | 1
5.45 | PRICES FOR MISCELLANEOUS STEEL WORKS FABRICATED IN LINE WITH SPECIFICATIONS, PRICES FOR SPECIAL TOWERS, SPECIAL EXTENSIONS AND MODIFICATIONS NB: These shall only be applicable where special towers, special extensions and modifications and any miscellaneous steel works have been approved by the Employer/Employer's Representative.
5.46 | Structural Mild Steel | tonnes | 5
5.47 | Structural High Tensile Steel | tonnes | 5
6 | INSTALLATION OF CONDUCTORS AND GROUND WIRES (OPGW)
| Complete stringing works for phase conductors and ground wire (OPGW) inclusive of related hardware and fittings installation. All costs for distribution from storage to individual tower sites and complete installation upto gantry according to the Specifications and approved drawings and plans of insulator string assemblies and fittings, extension links, armor rods, conductors and earthwires to correct sags, jumpers, sleevs, joint works, vibration dampers, counterweights, earth bonds, downleads et c as required and temporary guarding and scaffolding at crossings shall be included in the quoted prices. This shall include all requisite tests across joints for phase conductors as well as OTDR test for OPGW once concluded amongst others. | lump sum | 1
6.01 | ACSR Conductor Code Name "Condor" for the double circuit; 3 phases per circuit, triple bundle conductor per phase Note: Allowances for sagging, jumpers et c within the line and at substation ends shall be part of the quoted contract price per km of line route length. | route km | 2.5
6.02 | Optical Groundwire (OPGW) including all splicing and connections to joint boxes Note: Allowances for sagging, splicing as well as slacks allowed for maintenance purposes within the line and at substation ends shall be part of the quoted contract price per km of line route length. | route km | 2.5
6.03 | ACS Shield wire 7/3.26 mm Note: Allowances for sagging, jumpers et c within the line and at substation ends shall be part of the quoted contract price per km of line route length. | route km | 2.5
7 | FACTORY ACCEPTANCE TESTS (FAT) (NB: Quoted prices shall be all inclusive.)
7.1 | Tower and related stub materials as well as tower accessories FAT prior to shipment | lot | 1
7.2 | Factory inspections and test witnessing for Conductor per specifications | lot | 1
7.3 | Factory inspections and test witnessing for OPGW per specifications | lot | 1
7.4 | Factory inspections and test witnessing for Line conductor Insulators per specifications (across the various types and configurations) | lot | 1
7.5 | Line conductor hardwares and fittings FAT (Factory inspections and test witnessing after completing all type tests of this equipment / materials) | lot | 1
7.6 | OPGW fitting and accessories FAT (Factory inspections and test witnessing after completing all type tests of this equipment) | lot | 1
7.7 | ERS tower sets FAT (1No. Each for Suspension and Tension Sets) | lot | 1
7.8 | TOWER TYPE TESTS
7.8.1 | Tower type test for Suspension Tower Type S { i.e. Tower Type S (Basic Tower + 12m BE + 4m LE) } to destruction including supply, erection, recovery including all related costs as per employer requirements | each | 1
7.8.2 | Tower type tests to ultimate loading including supply, erection, dismantling, recovery including all related costs as per employer requirements for underlisted tension towers
| a) Tower Type T10 (Basic Tower + 12m BE + 4m LE) | each | 1
| b) Tower type T30 (Basic Tower + 12m BE + 4m LE) | each | 1
| c) Tower type T60/T90/Ttrm (Basic Tower + 12m BE + 4m LE) | each | 1
8 | Other Implementation Works
8.01 | Dismantling of the surplus part of the existing lines, packing and delivery to client's store and all associated works | lump sum | 1
8.02 | Re-tensioning a part of existing lines and all associated works in order to connect the new lines to the existing ones | lump sum | 1
8.03 | All necessary activities to connect all the project new transmission lines to the existing ones, including temporary by pass works, eventual connection to the substations | lump sum | 1
8.04 | Re-location of existing lines in Suswa and Isinya substation so as to ensure both circuits are connected to the 400kV bus bar | lump sum | 1
8.05 | ERS towers assembly and dissambly and handover to the employer | lump sum | 1
9 | Tree growing initiative
9.01 | Growing 50,000 trees | lump sum | 1
TOTAL PRICE SCHEDULE 4B KIMUKA TRANSMISSION LINE
Note on C68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PLease see comment in PS 1 B TL for towers to avoid any misunderstanding Reply: Addressed in schedule 1B
Note on D71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We may suggest lump sum Reply: These items are included to take care of site differences especially in site levels. Lump sum unit price negates this purpose. Our approach has been to remeasure the specific quantities at site.
Note on C159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please clarify 6 phase. the linre is 3 phase, triple bundle, double circuit???? Reply: Amended and made clearer

## Schedule 5_Grand Summary
SCHEDULE NO. 5
GRAND SUMMARY OF PRICES FOR KIMUKA SUBSTATION AND TRANSMISSION LINES
1 | 2 | 3 | 4 | 5
Item No | Description | Total Price
|  | FC1 | FC2 | KSh
1A | Total of Schedule No. 1A KIMUKA SS Plant, Equipment and Mandatory Spare Parts Supplied from Abroad
2A | Total of Schedule No. 2A KIMUKA SS Plant, Equipment and Mandatory Spare Parts Supplied from within Employer's Country
3A | Total of Schedule No. 3A KIMUKA SS Design Services
4A | Total of Schedule No. 4A KIMUKA SS Installation and other Services
A | TOTAL PRICES KIMUKA SUBSTATION (SCHEDULES 1A-4A) [1A+2A+3A+4A]
1B | Total of Schedule No. 1B KIMUKA TL Plant, Equipment and Mandatory Spare Parts Supplied from Abroad
2B | Total of Schedule No. 2B KIMUKA TL Plant, Equipment and Mandatory Spare Parts Supplied from within Employer's Country
3B | Total of Schedule No. 3B KIMUKA TL Design Services
4B | Total of Schedule No. 4B KIMUKA TL Installation and other Services
B | TOTAL PRICES KIMUKA TRANSMISSION LINE (SCHEDULES 1B-4B) [1B+2B+3B+4B]
C | TOTAL PRICES KIMUKA (SUBSTATION + TRANSMISSION LINE excluding provisional sum) [A+B]
D | PROVISIONAL SUM | 700000 |  | 10000000
E | TOTAL PRICE KIMUKA (SUBSTATION + TRANSMISSION LINE including provisional sum) [C+D]

## Schedule 6_ Optional Spares
SCHEDULE NO. 6
RECOMMENDED OPTIONAL SPARE PARTS
1 | 2 | 3 | 4 | 4 | 6 | 7 | 8 | 9
Item No | Description | Country of Origin | Unit | Estimated Quantity | Foreign Manufacture Price (CIP) | Local Manufacture Price (CIP) | Total Price for Estimated Quantity
[5 empty] | FC | KSh | FC | KSh
1 | 400kV Circuit breaker (3-phase) |  | No. | 1
2 | 220kV Circuit breaker (3-phase) |  | No. | 1
3 | 400kV Disconnector, motorised (3-phase) complete with one integral motorised earth switch |  | No. | 1
4 | 400kV Disconnector, motorised (3-phase) complete with two integral motorised earth switches |  | No. | 1
5 | 220kV Disconnector, motorised (3-phase) complete with one integral motorised earth switch |  | No. | 1
6 | 220kV Disconnector, motorised (3-phase) complete with two integral motorised earth switches |  | No. | 1
7 | 400kV Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 2
8 | Surge arrester (1-phase) including surge counter and earth leakage meter |  | No. | 1
9 | 400kV Post type current transformer Protection and Measuring Five Cores (1-phase) |  | No. | 3
10 | 400kV Post type current transformer High Accuracy Tariff Metering Two Cores (1-phase) |  | No. | 1
11 | 220kV Post type current transformer Protection and Measuring Five Cores (1-phase) |  | No. | 3
12 | 220kV Post type current transformer High Accuracy Tariff Metering OHL Two Cores (1-phase) |  | No. | 1
13 | Capacitive voltage transformer Protection and Measuring (1-phase) |  | No. | 3
14 | Capacitive voltage transformer High Accuracy Tariff Metering (1-phase) |  | No. | 1
15 | Capacitive voltage transformer Protection and Measuring (1-phase) |  | No. | 1
16 | Capacitive voltage transformer High Accuracy Tariff Metering (1-phase) |  | No. | 1
17 | 400kV Post insulator |  | % | 10
18 | 400kV Strain insulator |  | % | 10
19 | 220kV Post insulator |  | % | 10
20 | 220kV Strain insulator |  | % | 10
21 | 400kV Conductor - Tubular |  | % | 10
22 | 400kV Conductor - Stranded |  | % | 10
23 | 400kV Connectors - Tube |  | % | 10
24 | 400kV Connectors - Stranded |  | % | 10
25 | 220kV Conductor - Tubular |  | % | 10
26 | 220kV Conductor - Stranded |  | % | 10
27 | 220kV Connectors - Tube |  | % | 10
28 | 220kV Connectors - Stranded |  | % | 10
29 | 11kV cable sealing end (CSE) for 11kV side of 200MVA Auto Transformers and HV side of Auxiliary & Earthing Transformer |  | No. | 1
30 | Point On Wave (POW) Switching relay ( Synchronous Switching Controller) |  | No. | 1
31 | Line distance protection relay |  | No. | 1
32 | Line differential protection relay type 1 |  | No. | 1
33 | Line differential protection relay type 2 |  | No. | 1
34 | Bay Control and protection relay |  | No. | 2
35 | Transformer differential protection relay |  | No. | 1
36 | Bay module for busbar protection relay |  | No. | 2
37 | Station LAN Switches |  | No. | 1
38 | TARIFF METER |  | No. | 2
39 | 87HVC Connection Protection relay |  | No. | 1
40 | 50/51(N) Protection relay |  | No. | 1
TOTAL PRICE ITEMS

## Price Schedule_SUB_Summary
SUMMARY OF COST ESTIMATION FOR KIMUKA SUBSTATION |  |  |  | Contrator's Surplus Factor | Exchange rate
1 | 2 | 3 | 4 | Civil Works | USD to KES | 115.0512
Item No | Description | Total Price (1USD= ……... KSh)
|  | From Abroad (USD) | From Local (KSh) |  | KES to USD | 0.0086918
1 | Total of Schedule No. 1A KIMUKA SS Plant, Equipment and Mandatory Spare Parts Supplied from Abroad
Main Equipment
1.1 | 400kV PRIMARY PLANT
1.2 | 220kV PRIMARY PLANT
1.3 | AUTO TRANSFORMER (A.TR.)
1.4 | EARTHING & AUXILIARY TRANSFORMER
1.5 | NEUTRAL EARTHING RESISTOR
1.6 | 400kV PROTECTION SYSTEMS
1.7 | 220KV PROTECTION SYSTEMS
1.8 | 400/220kV SUBSTATION CONTROL SYSTEM
1.9 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
1.10 | TELECOMMUNICATION & NCC/RCC/NSCC
1.11 | LV CABLES AND ACCESSORIES
1.12 | EARTHING & LIGHTNING PROTECTION SYSTEMS
1.13 | 11KV CABLE SYSTEM
1.14 | SUPPORT STRUCTURES
1.15 | AUXILIARY SUPPLY
1.16 | TARIFF METERING
1.17 | FAULT MONITORING SYSTEM & PMU
1.18 | MISCELLANEOUS
1.19 | Site Transport as per Employer's Requirements, Clause 32
1.20 | Total of Main Equipment
Spare Parts
1.21 | 400kV PRIMARY PLANT
1.22 | 220kV PRIMARY PLANT
1.23 | AUTO TRANSFORMER (A.TR.)
1.24 | EARTHING & AUXILIARY TRANSFORMER
1.26 | 400kV PROTECTION SYSTEMS
1.27 | 220KV PROTECTION SYSTEMS
1.28 | 400/220kV SUBSTATION CONTROL SYSTEM
1.3 | TELECOMMUNICATION & NCC/RCC/NSCC
1.31 | LV CABLES AND ACCESSORIES
1.33 | 11KV CABLE SYSTEM
1.35 | AUXILIARY SUPPLY
1.36 | TARIFF METERING
1.37 | FAULT MONITORING SYSTEM & PMU
1.38 | MISCELLANEOUS
1.40 | Total of Spare Parts
2 | Total of Schedule No. 2A KIMUKA SS Plant, Equipment and Mandatory Spare Parts Supplied from Within the Employer's Country
Main Equipment
2.1 | 400kV PRIMARY PLANT
2.2 | 220kV PRIMARY PLANT
2.3 | AUTO TRANSFORMER (A.TR.)
2.4 | EARTHING & AUXILIARY TRANSFORMER
2.5 | NEUTRAL EARTHING RESISTOR
2.6 | 400kV PROTECTION SYSTEMS
2.7 | 220KV PROTECTION SYSTEMS
2.8 | 400/220kV SUBSTATION CONTROL SYSTEM
2.9 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
2.10 | TELECOMMUNICATION & NCC/RCC/NSCC
2.11 | LV CABLES AND ACCESSORIES
2.12 | EARTHING & LIGHTNING PROTECTION SYSTEMS
2.13 | 11KV CABLE SYSTEM
2.14 | SUPPORT STRUCTURES
2.15 | AUXILIARY SUPPLY
2.16 | TARIFF METERING
2.17 | FAULT MONITORING SYSTEM & PMU
2.18 | MISCELLANEOUS
2.19 | Site Transport as per Employer's Requirements, Clause 32
2.20 | Total of Main Equipment
Spare Parts
2.21 | 400kV PRIMARY PLANT
2.22 | 220kV PRIMARY PLANT
2.23 | AUTO TRANSFORMER (A.TR.)
2.24 | EARTHING & AUXILIARY TRANSFORMER
2.25 | 400kV PROTECTION SYSTEMS
2.26 | 220KV PROTECTION SYSTEMS
2.27 | 400/220kV SUBSTATION CONTROL SYSTEM
2.28 | TELECOMMUNICATION & NCC/RCC/NSCC
2.29 | LV CABLES AND ACCESSORIES
2.30 | 11KV CABLE SYSTEM
2.31 | AUXILIARY SUPPLY
2.32 | TARIFF METERING
2.33 | FAULT MONITORING SYSTEM & PMU
2.34 | MISCELLANEOUS
2.35 | Total of Spare Parts
3 | Total of Schedule No. 3A KIMUKA SS Design Services
4 | Total of Schedule No. 4A KIMUKA SS Civil Works, Installation and other Services
4.1 | 400kV PRIMARY PLANT
4.2 | 220kV PRIMARY PLANT
4.3 | AUTO TRANSFORMER (A.TR.)
4.4 | EARTHING & AUXILIARY TRANSFORMER
4.5 | NEUTRAL EARTHING RESISTOR
4.6 | 400kV PROTECTION SYSTEMS
4.7 | 220KV PROTECTION SYSTEMS
4.8 | 400/220kV SUBSTATION CONTROL SYSTEM
4.9 | CONTROL AND PROTECTION SYSTEM IN EXISTING REMOTE SUBSTATIONS
4.10 | TELECOMMUNICATION & NCC/RCC/NSCC
4.11 | LV CABLES AND ACCESSORIES
4.12 | EARTHING & LIGHTNING PROTECTION SYSTEMS
4.13 | 11KV CABLE SYSTEM
4.14 | SUPPORT STRUCTURES
4.15 | CIVIL WORKS
4.16 | AUXILIARY SUPPLY
4.17 | TARIFF METERING
4.18 | FAULT MONITORING SYSTEM & PMU
4.19 | MISCELLANEOUS
4.20 | Mobilization, Site Transport, Site Office and Permanent Living Provision as per Employer's Requirements, Clause 31, 32 & 34 of Part 2-A of Employer's Requirements
4.22 | TRAINING
4.23 | INTERNSHIP and EMPLOYMENT
TOTAL PRICES KIMUKA SUBSTATION (SCHEDULES 1A-4A)
TOTAL PRICE KIMUKA (SUBSTATION) IN KENYAN SHILLINGS

## Price Schedule_TL_Summary
SUMMARY OF COST ESTIMATION FOR KIMUKA TRANSMISSION LINES
1 | 2 | 3 | 4
Item No | Description | Total Price (1USD= ……... KSh)
|  | From Abroad (USD) | From Local (KSh)
1 | Total of Schedule No. 1B Plant, Equipment and Mandatory Spare Parts Supplied from Abroad (CIP)
1.1 | Tower, Stub, Accessories and Grounding
1.2 | Conductor
1.3 | ShieldWire
1.4 | OPGW
1.5 | Insulator and Fittings
2 | Total of Schedule No. 2B Plant, Equipment and Mandatory Spare Parts Supplied from Within the Client's Country (DAP)
2.1 | Tower, Stub, Accessories and Grounding
2.2 | Conductor
2.3 | ShieldWire
2.4 | OPGW
2.5 | Insulator and Fittings
3 | Total of Schedule No. 3B Design Services
3.1 | Tower Design
3.2 | Foundation Design
3.3 | Conductor, shield wire and OPGW Design
3.4 | Line Profiling (preparation of plan and profile drawings, tower spotting and tower schedule in PLS-CADD software)
4 | Total of Schedule No. 4B Installation and other Services
4.1 | General Works (Routing, Geology, Surveying, etc.)
4.2 | Foundation
4.3 | Tower Erection
4.4 | Conductor Stringing
4.5 | ShieldWire Stringing
4.6 | OPGW Stringing
4.7 | Other Implementation Works
TOTAL PRICES KIMUKA LILO WORKS (SCHEDULES 1B-4B)
TOTAL PRICE KIMUKA LILO (SCHEDULES 1B-4B) IN KENYAN SHILLINGS