|  | 132kV CAPACITIVE VOLTAGE TRANSFORMERS |  |  |  |
| --- | --- | --- | --- | --- |
|  | General |  |  |  |
| 5.1 | Manufacturer |  |  |  |
| 5.2 | Place of manufacturing |  |  |  |
| 5.3 | Type of CVT |  | Single-phase/self-Cooled |  |
| 5.4 | Applicable standard |  | IEC 61869-1/-5 |  |
| 5.5 | Rated voltage | kV rms | 145 |  |
| 5.6 | System Voltage | kV | 132 |  |
| 5.7 | Rated frequency | Hz | 50 |  |
| 5.8 | Max. and min. ambient temperatures used for design | °C | Acc. to Section1 |  |
| 5.9 | Class (indoor/ outdoor ) |  | Outdoor |  |
| 5.8 | Type (Oil-immersed / dry) |  | Oil-immensed/ Oil-impregnated paper |  |
| 5.9 | Maximum permissible partial discharge level at Um | pC | 10 |  |
| 5.10 | Maximum permissible partial discharge level at 1.2Um /Ö3 | pC | 5 |  |
| 5.11 | Whether withstanding in load combinations of earthquake , wind , short circuit? (Yes / No) | (Yes / No) | Yes |  |
| 5.12 | Altitude above sea level | m | Acc. to Section1 |  |
| 5.13 | Manufacturer quality system in accordance with ISO 9000 | Yes/No | Yes |  |
| 5.13.1 | Date of issue |  | Latest |  |
| 5.13.2 | Validity |  |  |  |
| 5.13.3 | Certificate attached to the offer | Yes/No | Yes |  |
|  | Insulation ratings |  |  |  |
| 5.14 | Basic insulation level (at site condition) | kV peak | 750 |  |
| 5.15 | Switching impulse withstand voltage (at site condition ) | kV peak | - |  |
| 5.16 | One minute power frequency withstand voltage (at site condition ) | kV rms | 325 |  |
| 5.17 | Power frequency withstand voltage between secondaries and secondary to earth | kV rms |  |  |
| 5.18 | Rated voltage factor |  |  |  |
| 5.18.1 | Continuous |  | 1.2 |  |
| 5.18.2 | 30 seconds |  | 1.5 |  |
| 5.19 | Minimum HV terminal withstand |  |  |  |
| 5.19.1 | Static terminal load |  | 1000 |  |
| 5.19.2 | Dynamic terminal load |  | 2000 |  |
| 5.20 | Max. RIV measured at 1.2 highest system voltage , 1 Mega-Hz acc. to CISPR | μV |  |  |
|  | Burdens and accuracies |  |  |  |
|  | 3-Winding CVT |  | 3 |  |
| 5.21 | Number of secondary windings |  |  |  |
| 5.22 | Accuracy class for |  | Acc. to SLD |  |
| 5.22.1 | Winding 1 |  | Acc. to SLD |  |
| 5.22.2 | Winding 2 |  | Acc. to SLD |  |
| 5.22.3 | Winding 3 |  |  |  |
| 5.23 | Rated primary voltage | KVrms | 132/√3 |  |
| 5.24 | Rated secondary voltage | KVrms | 0.11/√3 |  |
| 5.25 | Rated burden for |  |  |  |
| 5.25.1 | Winding 1 | VA | Acc. to SLD |  |
| 5.25.2 | Winding 2 | VA | Acc. to SLD |  |
| 5.25.3 | Winding 3 | VA | Acc. to SLD |  |
| 5.26 | Continuous thermal burden of |  |  |  |
| 5.26.1 | Winding 1 alone | VA |  |  |
| 5.26.2 | Winding 2 alone | VA | 2 |  |
|  | 2-Winding CVT |  |  |  |
| 5.27 | Number of secondary windings |  | Acc. to SLD |  |
| 5.28 | Accuracy class for |  |  |  |
| 5.28.1 | Winding 1 |  | Acc. to SLD |  |
| 5.28.2 | Winding 2 |  | Acc. to SLD |  |
| 5.29 | Rated primary voltage | KVrms | 132/√3 |  |
| 5.2.30 | Rated secondary voltage | KVrms | 0.11/√3 |  |
| 5.31 | Rated burden for |  |  |  |
| 5.31.1 | Winding 1 | VA | Acc. to SLD |  |
| 5.31.2 | Winding 2 | VA | Acc. to SLD |  |
| 5.32 | Continuous thermal burden of |  |  |  |
| 5.32.1 | Winding 1 alone | VA | During detailed engineering |  |
| 5.32.2 | Winding 2 alone | VA | During detailed engineering |  |
| 5.33 | Type of system grounding |  | Effective |  |
| 5.34 | Type of connection |  | phase to ground |  |
| 5.35 | Connections |  | (screw and bolt) |  |
| 5.35.1 | Primary |  | Standard terminal block contact |  |
| 5.35.2 | Secondary |  | Standard terminal block |  |
| 5.36 | Type of protection device in secondary side |  | MCB with auxiliary |  |
| 5.37 | Total continuous thermal burden of secondary windings | VA |  |  |
| 5.37.1 | Primary |  | During detailed engineering |  |
| 5.37.2 | Secondary |  | During detailed engineering |  |
|  | Other Characteristics |  |  |  |
| 5.38 | Temperature rise at rated burden and at 1.2 times rated primary voltage and ambient temperature | K | 60K Wind. 50K Oil Max |  |
| 5.39 | Permissible secondary short circuit time with rated primary voltage | sec | 1 |  |
| 5.40 | Short circuit impedance | Ohm | 0.25 (Max) |  |
| 5.41 | Method of suppressing for ferro-resonance |  | RLC Dumping |  |
| 5.42 | Available ranges of high voltage capacitor | pF | 35*10-4 |  |
| 5.43 | Coupling capacitor * | pF | Max (10000) |  |
| 5.44 | Loss angle at rated voltage |  | Max (40) |  |
| 5.45 | Frequency range for PLC use | KHz |  |  |
| 5.46 | Equipment series resistance for 35-450 KHz | Ohm |  |  |
| 5.47 | Natural frequency | MHz |  |  |
| 5.48 | Intermediate stage voltage | kV |  |  |
| 5.49 | Attenuation of intermediate voltage transformer within 35-450 KHz | dB |  |  |
| 5.50 | Max. insertion loss when used for PLC | dB |  |  |
| 5.51 | Whether intermediate tap is brought out? (Yes / No) |  |  |  |
|  | Insulator columns |  |  |  |
| 5.52 | Manufacturer |  |  |  |
| 5.53 | Place of manufacturing |  |  |  |
| 5.54 | Type designation |  |  |  |
| 5.55 | Material |  | Porcelain |  |
| 5.56 | Min. creepage distance | mm | 4495 |  |
| 5.57 | Protected creepage distance | mm |  |  |
| 5.58 | Color |  | Brown |  |
|  | Miscellaneous |  |  |  |
| 5.59 | Type and manufacturer of oil for capacitor section |  |  |  |
| 5.60 | Type and manufacturer of oil for intermediate section |  |  |  |
| 5.61 | Whether oil level indicator is provided? (Yes / No) | (Yes / No) | Yes |  |
| 5.62 | Class and grade of insulation material used in capacitors |  |  |  |
| 5.63 | Permitted inclination during transport/ storage | Degree |  |  |
| 5.64 | Material of windings |  |  |  |
| 5.65 | Whether CVT is designed to mount line trap on top? (Yes / No) |  |  |  |
| 5.66 | Permissible force at HV terminals |  |  |  |
| 5.66.1 | Static at any direction | N |  |  |
| 5.66.2 | Dynamic at any direction | N |  |  |
| 5.67 | Total weight | kg |  |  |
| 5.68 | Total oil weight | kg |  |  |
| 5.69 | Overall height | mm |  |  |
| 5.70 | Overall width | mm |  |  |
| 5.71 | Max. package dimensions ready for shipment | m3 |  |  |
| 5.72 | Washable in service? (Yes / No) |  |  |  |

|  | 33kV VOLTAGE TRANSFORMERS |  |  |  |
| --- | --- | --- | --- | --- |
|  | General |  |  |  |
| 5.1 | Manufacturer |  |  |  |
| 5.2 | Place of manufacturing |  |  |  |
| 5.3 | Type of VT |  | Single-phase/self-Cooled |  |
| 5.4 | Applicable standard |  | IEC 61869-1/-5 |  |
| 5.5 | Rated voltage | kV rms | 36 |  |
| 5.6 | System Voltage | kV | 33 |  |
| 5.7 | Rated frequency | Hz | 50 |  |
| 5.8 | Max. and min. ambient temperatures used for design | °C | Acc. to Section 1 |  |
| 5.9 | Class (indoor/ outdoor ) |  | Outdoor |  |
| 5.8 | Type (Oil-immersed / dry) |  | Oil-immersed/ Oil-impregnated paper |  |
| 5.9 | Maximum permissible partial discharge level at Um | pC | 10 |  |
| 5.10 | Maximum permissible partial discharge level at 1.2Um /Ö3 | pC | 5 |  |
| 5.11 | Whether withstanding in load combinations of earthquake , wind , short circuit? (Yes / No) | (Yes / No) | Yes |  |
| 5.12 | Altitude above sea level | m | Acc. to Section 1 |  |
| 5.13 | Manufacturer quality system in accordance with ISO 9000 | Yes/No | Yes |  |
| 5.13.1 | Date of issue |  | Latest |  |
| 5.13.2 | Validity |  |  |  |
| 5.13.3 | Certificate attached to the offer | Yes/No | Yes |  |
|  | Insulation ratings |  |  |  |
| 5.14 | Basic insulation level (at site condition) | kV peak | 250 |  |
| 5.15 | Switching impulse withstand voltage (at site condition ) | kV peak | - |  |
| 5.16 | One minute power frequency withstand voltage (at site condition ) | kV rms | 95 |  |
| 5.17 | Power frequency withstand voltage between secondaries and secondary to earth | kV rms |  |  |
| 5.18 | Rated voltage factor |  |  |  |
| 5.18.1 | Continuous |  | 1.2 |  |
| 5.18.2 | 30 seconds |  | 1.5 |  |
| 5.19 | Minimum MV terminal withstand |  |  |  |
| 5.19.1 | Static terminal load |  |  |  |
| 5.19.2 | Dynamic terminal load |  |  |  |
| 5.20 | Max. RIV measured at 1.2 highest system voltage , 1 Mega-Hz acc. to CISPR | μV |  |  |
|  | Burdens and accuracies |  |  |  |
|  | 3-Winding VT |  | 3 |  |
| 5.21 | Number of secondary windings |  |  |  |
| 5.22 | Accuracy class for |  |  |  |
| 5.22.1 | Winding 1 |  | Acc. to SLD |  |
| 5.22.2 | Winding 2 |  | Acc. to SLD |  |
| 5.22.3 | Winding 3 |  | Acc. to SLD |  |
| 5.23 | Rated primary voltage | KVrms | 33/√3 |  |
| 5.24 | Rated secondary voltage | KVrms | 0.11/√3 |  |
| 5.25 | Rated burden for |  |  |  |
| 5.25.1 | Winding 1 | VA | Acc. to SLD |  |
| 5.25.2 | Winding 2 | VA | Acc. to SLD |  |
| 5.25.3 | Winding 3 | VA | Acc. to SLD |  |
| 5.26 | Continuous thermal burden of |  |  |  |
| 5.26.1 | Winding 1 alone | VA | During detailed engineering |  |
| 5.26.2 | Winding 2 alone | VA | During detailed engineering |  |
|  | 2-Winding VT |  |  |  |
| 5.27 | Number of secondary windings |  | Acc. to SLD |  |
| 5.28 | Accuracy class for |  |  |  |
| 5.28.1 | Winding 1 |  | Acc. to SLD |  |
| 5.28.2 | Winding 2 |  | Acc. to SLD |  |
| 5.29 | Rated primary voltage | KVrms | 33/√3 |  |
| 5.2.30 | Rated secondary voltage | KVrms | 0.11/√3 |  |
| 5.31 | Rated burden for |  |  |  |
| 5.31.1 | Winding 1 | VA | Acc. to SLD |  |
| 5.31.2 | Winding 2 | VA | Acc. to SLD |  |
| 5.32 | Continuous thermal burden of |  |  |  |
| 5.32.1 | Winding 1 alone | VA | Acc. to SLD |  |
| 5.32.2 | Winding 2 alone | VA | Acc. to SLD |  |
| 5.33 | Type of system grounding |  | Effective |  |
| 5.34 | Type of connection |  | Phase to gnd |  |
| 5.35 | Connections |  |  |  |
| 5.35.1 | Primary |  | Standard terminal block (screw and bolt) |  |
| 5.35.2 | Secondary |  | Standard terminal block (screw and bolt) |  |
| 5.36 | Type of protection device in secondary side |  | MCB with auxiliary contact |  |
| 5.37 | Total continuous thermal burden of secondary windings | VA |  |  |
| 5.37.1 | Primary |  | During detailed engineering |  |
| 5.37.2 | Secondary |  | During detailed engineering |  |
|  | Other Characteristics |  |  |  |
| 5.38 | Temperature rise at rated burden and at 1.2 times rated primary voltage and ambient temperature | K | 60K Wind. 50K Oil Max |  |
| 5.39 | Permissible secondary short circuit time with rated primary voltage | sec | 1 |  |
| 5.40 | Short circuit impedance | Ohm | Max(0.25) |  |
| 5.41 | Method of suppressing for ferro-resonance |  | RLC Dumping |  |
| 5.42 | Available ranges of high voltage capacitor | pF | 35*10-4 |  |
| 5.43 | Coupling capacitor * | pF | Max (10000) |  |
| 5.44 | Loss angle at rated voltage |  | Max(40) |  |
| 5.45 | Frequency range for PLC use | KHz | NA |  |
| 5.46 | Equipment series resistance for 35-450 KHz | Ohm |  |  |
| 5.47 | Natural frequency | MHz |  |  |
| 5.48 | Intermediate stage voltage | kV |  |  |
| 5.49 | Attenuation of intermediate voltage transformer within 35-450 KHz | dB |  |  |
| 5.50 | Max. insertion loss when used for PLC | dB |  |  |
| 5.51 | Whether intermediate tap is brought out? (Yes / No) |  |  |  |
|  | Insulator columns |  |  |  |
| 5.52 | Manufacturer |  |  |  |
| 5.53 | Place of manufacturing |  |  |  |
| 5.54 | Type designation |  |  |  |
| 5.55 | Material |  |  |  |
| 5.56 | Min. creepage distance | mm | 1256 |  |
| 5.57 | Protected creepage distance | mm |  |  |
| 5.58 | Color |  | Brown |  |
|  | Miscellaneous |  |  |  |
| 5.59 | Type and manufacturer of oil for capacitor section |  |  |  |
| 5.60 | Type and manufacturer of oil for intermediate section |  |  |  |
| 5.61 | Whether oil level indicator is provided? (Yes / No) | (Yes / No) | Yes |  |
| 5.62 | Class and grade of insulation material used in capacitors |  |  |  |
| 5.63 | Permitted inclination during transport/ storage | Degree |  |  |
| 5.64 | Material of windings |  |  |  |
| 5.66 | Permissible force at MV terminals |  |  |  |
| 5.66.1 | Static at any direction | N |  |  |
| 5.66.2 | Dynamic at any direction | N |  |  |
| 5.67 | Total weight | kg |  |  |
| 5.68 | Total oil weight | kg |  |  |
| 5.69 | Overall height | mm |  |  |
| 5.70 | Overall width | mm |  |  |
| 5.71 | Max. package dimensions ready for shipment | m3 |  |  |
| 5.72 | Washable in service? (Yes / No) |  |  |  |